## Guidance Notes
GREEN MARK INTERNATIONAL IN-OPERATION
Guidance Notes
1 | GM International In-Operation aims to encourage buildings that have been previously certified before to continuously improve and maintain their performance.
2 | The assessment will be based on measured data. No letter of commitment or undertaking will be accepted for GM International In-Operation certification. Supporting documents such as OSE report, IAQ audit, POE survey shall be completed prior to the GM assessment.
3 | Based on the actual performance, the GM ratings can be upgraded or downgraded. For example, if a building that has been previously certified as GM Gold rating, but if the actual performance at the time of assessment meets the GM International Platinum requirement, its rating can be upgraded to Platinum.
4 | How to calculate EUI for EE pathway1? Energy Use Intensity (EUI) express a building's energy use over a period of one year. It's calculated by dividing the total energy consumed by the building in one year (measured in kWh) by the total gross floor area (GFA) of the building (m2). You can get your most recent one year's energy use from your utility bills and divided by GFA to get the most recent EUI. Note: to use EUI pathway, the occupancy rate must be higher than 60%.
5 | TSE stands for Total System Efficiency. For water-cooled or air-cooled system, it is the sum of the efficiency values of both chiller plant and air side; for VRF or unitary system, TSE is the sum of efficiency values of the CU and FCUs (or AHUs if applicable).
6 | District Cooling System (DCS) refers to the supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install separate chiller plant or unitary system. This is different from buildings’ in-house air-conditioning plant, in part or in full, being maintained and operated by a third party.
7 | Under EE Pathway 2, projects shall meet the minimum requirements i.e. the TSE should be better than 0.9 kW/RT regardless of the project's previous GM rating.
8 | Under TSE requirement in GM International In-Operation, is it required to measure TSE for all types of systems i.e. water cooled, air cooled and Variable Refrigerant Flow (VRF) system? The answer is YES for both water and air side efficiencies. However for VRF system, the CU efficiency can be based on catalogue or via calculation. In the future, projects with VRF system may need to measure their CUs’ efficiency. For projects which do not have technical specifications of their existing VRF equipment, the VRF efficiency will be calculated based on nameplate power and cooling load. For buildings with permanent M&V for VRF system, such as suppliers' monitoring system, the efficiency should be based on the measured data.
9 | For projects without permanent M&V for air side, how can the air side efficiency be measured? For projects without permanent M&V for airside, 3rd party energy audit for air side is required. Please see detailed requirement below: a) For AHUs (A) with Variable Speed Drives (VSD), power readings should be downloaded from the VSD of all AHUs to calculate air side efficiency; b) For AHUs (A) without VSD, measurement must be taken with the sampling size of 30% for AHUs of each size (in terms of cooling capacity) with trend logging of power and cooling load for one week. The minimum number of AHUs to be measured is 5 and capped at max of 20 AHUs. When the actual number of AHUs on site is less than 5, all AHUs need to be measured. c) For FCUs (B), power readings can be based on the nameplate Motor Power or catalogue data. d) The Building Cooling Load (C) shall be the building cooling load measured from the chiller plant. e) Air-side efficiency at building level is the summation of (∑A + ∑B) / C This is valid till the next major retrofit when the building will be subject to GM International full certification.
10 | Does OSE Report need to be endorsed by Energy Auditor (EA) or PE (Mech) for GM International In-Operation? Yes, OSE reports shall be endorsed by Energy Auditor (EA) or local PE (Mech).

## 1. Project Details
GM International In-Operation is applicable for Existing Buildings (a) which have previously attained Green Mark certification, (b) applying for re-certification and (c) have not done any major retrofit to the building's chilled water system.
GM International In-Operation
Project Details |  | Possible inputs
GM Reference No
Building name
Country
Type of Building (Office or hotel or retail, etc.) |  | Office / Retail / Hotel / Mixed Office + Retail
GFA (m2)
Carpark Area (m2)
Air-conditioned Area (m2)
Building Key Performance Data:
Type of Aircon system |  | Central Water-cooled Chiller Plant / VRF System / Unitary System
Building cooling load (RT)
Chiller configuration (e.g. 3 nos. x 500RT)
Cooling load / aircon area (W/m2) | #DIV/0!
Air-conditioning system efficiency (kW/RT) (Plant or CU)
Air Distribution system efficiency (kW/RT)
Total System Efficiency, TSE (kW/RT)
Total Building Energy consumption (kWh/yr)
EUI (kWh/m2/yr) - based on latest annual building consumption

## 2. EE requirement
ENERGY EFFICIENCY REQUIREMENTS
Rating | Certified* & Gold* | GoldPLUS | Platinum | SLE
% Energy efficiency improvement over 2005 levels* | 40% | 50% | 55% | 60%
Applicable EE Pathways: Pathway 1 – EUI; Pathway 2 – Fixed metrics
*Aligns with mandatory minimum energy efficiency requirements to raise energy performance standards of existing buildings

## 2.1 EE Pathway1
PATHWAY 1 ENERGY USE INTENSITY (EUI)
EUI Pathway1: for buildings with in-house Chilled water systems or other cooling systems |  |  |  |  | EUI Pathway1: for buildings supplied by DCS*
Building Type | Certified & Gold | Goldplus | Platinum | SLE | Building Type | Certified & Gold | Goldplus | Platinum | SLE
Commercial |  |  |  |  | Commercial
Office Buildings (Large) | 155 | 155 | 140 | 115 | Office Buildings (Large) | 100 | 100 | 90 | 80
Office Buildings (Small) | 135 | 135 | 120 | 100 | Office Buildings (Small) | 90 | 90 | 80 | 75
Hotels (Large) | 230 | 230 | 220 | 190 | Hotels (Large) | 149.5 | 149.5 | 134.55 | 119.6
Hotels (Small) | 180 | 180 | 160 | 140 | Hotels (Small) | 120.25 | 120.25 | 110 | 95
Retail Malls | 240 | 240 | 210 | 160 | Retail Malls | 160 | 160 | 144 | 128
Educational |  |  |  |  | Educational
Tertiary Institutions (University & Polytechnics) | 130 | 130 | 120 | 90 | Tertiary Institutions (University & Polytechnics) | Nil
Schools and Colleges | 110 | 110 | 100 | 80 | Schools and Colleges
Healthcare |  |  |  |  | Healthcare
Hospitals (Private and General) | 375 | 375 | 340 | 300 | Hospitals (Private and General) | 295 | 245 | 230 | 210
Community Hospitals | 230 | 230 | 210 | 185 | Community Hospitals | 180 | 149.5 | 140 | 129.5
Polyclinic | 150 | 150 | 135 | 120 | Polyclinic | 120 | 100 | 90.45 | 85
Nursing/Youth Homes | 90 | 90 | 80 | 70 | Nursing/Youth Homes | 70 | 60 | 55 | 50
Other Non-Residential |  |  |  |  | Other Non-Residential
Mixed Develpments | by GFA mix |  |  |  | Mixed Develpments | by GFA mix
Community Centres | 150 | 150 | 125 | 110 | Community Centres | 120 | 100 | 90 | 80
Civic Buildings | 80 | 80 | 70 | 60 | Civic Buildings | 65 | 50 | 45 | 40
Cultural Institution | 180 | 180 | 140 | 120 | Cultural Institution | 140 | 115 | 100 | 85
Sports and Recreation Centres | 110 | 110 | 80 | 50 | Sports and Recreation Centres | 85 | 70 | 65 | 35
Religious/ Place of Worship | NA |  |  |  | Religious/ Place of Worship | NA
Industrial |  |  |  |  | Industrial
High Tech Industrial | NA |  |  |  | High Tech Industrial | NA
Light Industrial |  |  |  |  | Light Industrial
Warehouses, Workshops and Others |  |  |  |  | Warehouses, Workshops and Others
Additional Notes
Non Residential Buildings Minimum TSE |  | 0.9 kW/RT
For ENRB using DCS*, air side minimum efficiency |  | 0.25 kW/RT
On-site RE is included in EUI (net off) |  | On-site RE
EUI measured for EB and In Operation - occupancy rate |  | >60%
Excludes EV charging station consumption
EUI calculation:
Energy Utilisation Intensity =Total Building Energy Consumption of one year (kWhyr) / GFA (m2) Please use the most recent 12 months' energy consumption (occupancy rate >60%) to calculate the most recent EUI.
*DCS refers to the supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install their own air-conditioning plant. This is different from buildings’ in-house air-conditioning plant, in part or in full, being maintained and operated by a third party.

## 4. EUI (hidden)
Energy Utility Index (3 Years Electricity Bill)
Energy Consumption (1st Year, Baseline)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'14 | 1228556 | 13401 | 1215155
Yearly Consumption | 1228556 | 13401 | 1215155
Energy Consumption (2nd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'15 | 1096746 | 9944 | 1086802
Yearly Consumption | 1096746 | 9944 | 1086802
Baseline Improvement | 10.73%
Energy Consumption (3rd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'16 | 1093303 | 11049 | 1082254
Yearly Consumption | 1093303 | 11049 | 1082254
Baseline Improvement | 11.01%
Computation of Energy Untility Index (EUI) based on area (kW/m²/year)
| Year 1 | Year 2 | Year 3
Total Building Energy Consumption (kWh) | 1228556 | 1096746 | 1093303
Gross Floor Area,m² (GFA) | 0
Energy Utility Index, EUI | #DIV/0! | #DIV/0! | #DIV/0!
Deviation | Baseline | #DIV/0! | #DIV/0!
Reasons, if deviation > ± 5% | -

## 2.2 EE Pathway2
PATHWAY 2 - FIXED METRICS
(1) For buildings with in-house Chilled water systems or other cooling systems
ACMV Total System Efficiency, TSE (in kW/RT)
Building types | Certified & Gold | GoldPLUS | Platinum | SLE
For commerical buildings | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.74 | 0.68
For Healthcare | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.75 | 0.7
For Educational building | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.75 | 0.7
For High Tech/ High intensity | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.78 | 0.75
For Light industry/ Warehouse | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.75 | 0.7
For other non Resi buildings | TSE 0.9 or Plant efficiency of 0.65 | 0.8 | 0.75 | 0.7
(2) For buildings served by DCS2
Airside Efficiency (in kW/RT)
PARAMETER | Certified & Gold | GoldPLUS | Platinum | SLE
Air side efficiency (kW/RT) | 0.25 | 0.2 | 0.18 | 0.16
Note: 1TSE is Total System Efficiency, including the efficiency from both chilled water plant and air side for water-cooled system; for VRF system, TSE includes the CU and FCUs efficiency 2DCS refers to the supply of chilled water for cooling purpose from a central source to multiple buildings through a network of pipes. Individual users purchase chilled water from the district cooling system operator and do not need to install their own air-conditioning plant. This is different from buildings’ in-house air-conditioning plant, in part or in full, being maintained and operated by a third party. 3For GM International full certification, M&V is required for TSE calculation/measurement; However, for project previously certified under legacy criteria, applying re-certification based on GM International In-Operation, air side efficiency can be done by third party energy audit. The methodology of air side measurement and its sampling size should refer to the Guidance Notes.

## 3.1 OSE Report & TSE
Summary of OSE/Energy Audit Report (including airside efficiency) |  | Use "Insert..Object..Create from File" command if macro execution is disabled
Daily Average Reading | Period |  |  | Unit
| Day Time^ | Night Time~ | 24-hours (if applicable)
Cooling Load |  |  |  | RT
Cooling Load Density (Air-con area) |  |  |  | m2/RT
Energy Consumption from Chilled water side (Chillers, Pumps, CTs) |  |  |  | kW
Chilled water supply temperature |  |  |  | oC
Chilled water return temperature |  |  |  | oC
Chilled water delta T |  |  |  | oC
Chilled water flow rate |  |  |  | l/s
Chilled water flow rate vs cooling load |  |  |  | USgpm/RT
*Condenser heat rejection |  |  |  | HRT
*Condenser water supply temperature |  |  |  | oC
*Condenser water return temperature |  |  |  | oC
*Condenser water delta T |  |  |  | oC
*Condenser water flow rate |  |  |  | l/s
*Condenser water flow rate vs cooling load |  |  |  | USgpm/RT
Chiller(s) efficiency |  |  |  | kW/RT
Chilled water pump(s) efficiency |  |  |  | kW/RT
*Condenser water pump(s) efficiency |  |  |  | kW/RT
*Cooling tower(s) efficiency |  |  |  | kW/RT
Overall chiller plant system efficiency |  |  |  | kW/RT
Energy consumption from airside |  |  |  | kW
Air Distribution system efficiency |  |  |  | kW/RT
Total System Efficiency |  |  |  | kW/RT
*Not applicable to Air-cooled Chilled Water Plant
~For hotels and other developments with 24-hour operations only, night time shall refer to the period from 11pm-7am
^ For hotels and other developments with 24-hour operations, day-time shall refer to the period from 7am–11pm; for all other developments, daytime shall refer to the normal operating hours stipulated below:-
Office Buildings: Monday to Friday : 9am to 6pm Retail Malls: Monday to Sunday : 10am to 9pm Other building types: To be determined based on the operating hours.
Summary of Heat Balance
| Data | Unit | Formula
Sum of total electrical energy used |  | kWh | (A)
Sum of total cooling produced |  | RTh | (B)
Sum of total heat rejected |  | RTh | (C)
Chiller Plant Efficiency |  | kW/RT | (A) / (B)
Total Heat Balance Data Count |  | - | (D)
Data Count > + 5% error |  | - | (E)
Data Count < - 5% error |  | - | (F)
Data Count within ±5% error |  | - | (G) = (D) – (E) – (F)
% Heat Balance within ±5% error |  | % | 100 x (G) / (D)
Click to Attach
Audit Report

## 3.2 Temperature Sensors
Temperature Sensors Check |  |  |  | VERIFICATION OF TEMPERATURE SENSORS ACCURACY
Date: | 2/11/2021 & 25/1/2022 |  |  | Name of Energy Auditor : |  |  |  | Date of sensors verifications :
Please replace the figures in the table with your measured data.
CHWS-1 Temperature (°C) |  |  |  | CHWS-2 Temperature (°C) |  |  |  | CHWS-3 Temperature (°C)
Time | BMS | FLUKE | ABS Diff | Time | BMS | FLUKE | ABS Diff | Time | BMS | FLUKE | ABS Diff
15:01 | 7.2738 | 7.232 | 0.0418 | 11:44 | 7.361 | 7.42 | 0.059 | 11:24 | 7.3974 | 7.393 | 0.0044
15:01 | 7.257 | 7.202 | 0.055 | 11:44 | 7.3811 | 7.407 | 0.0259 | 11:25 | 7.3864 | 7.38 | 0.0064
15:01 | 7.2149 | 7.181 | 0.0339 | 11:44 | 7.3832 | 7.388 | 0.0048 | 11:25 | 7.3811 | 7.381 | 0.0001
15:01 | 7.1867 | 7.114 | 0.0727 | 11:44 | 7.385 | 7.387 | 0.002 | 11:25 | 7.378 | 7.357 | 0.021
15:01 | 7.1319 | 7.211 | 0.0791 | 11:44 | 7.3478 | 7.36 | 0.0122 | 11:25 | 7.3558 | 7.344 | 0.0118
15:01 | 7.2541 | 7.232 | 0.0221 | 11:45 | 7.2988 | 7.319 | 0.0202 | 11:25 | 7.347 | 7.364 | 0.017
15:02 | 7.2292 | 7.209 | 0.0202 | 11:45 | 7.2933 | 7.357 | 0.0637 | 11:25 | 7.3878 | 7.378 | 0.0098
15:02 | 7.2416 | 7.246 | 0.0044 | 11:45 | 7.3526 | 7.37 | 0.0174 | 11:26 | 7.3879 | 7.391 | 0.0031
15:02 | 7.292 | 7.251 | 0.041 | 11:45 | 7.3675 | 7.373 | 0.0055 | 11:26 | 7.3707 | 7.37 | 0.0007
15:02 | 7.2396 | 7.22 | 0.0196 | 11:45 | 7.3427 | 7.355 | 0.0123 | 11:26 | 7.3513 | 7.342 | 0.0093
15:02 | 7.2525 | 7.184 | 0.0685 | 11:45 | 7.3207 | 7.351 | 0.0303 | 11:26 | 7.3256 | 7.304 | 0.0216
15:02 | 7.1839 | 7.198 | 0.0141 | 11:46 | 7.3078 | 7.32 | 0.0122 | 11:26 | 7.2971 | 7.289 | 0.0081
15:03 | 7.2359 | 7.218 | 0.0179 | 11:46 | 7.2864 | 7.293 | 0.0066 | 11:26 | 7.2854 | 7.28 | 0.0054
15:03 | 7.2337 | 7.221 | 0.0127 | 11:46 | 7.2745 | 7.289 | 0.0145 | 11:27 | 7.2719 | 7.268 | 0.0039
15:03 | 7.2395 | 7.378 | 0.1385 | 11:46 | 7.2912 | 7.298 | 0.0068 | 11:27 | 7.3051 | 7.303 | 0.0021
15:03 | 7.424 | 7.431 | 0.007 | 11:46 | 7.2674 | 7.325 | 0.0576 | 11:27 | 7.3103 | 7.306 | 0.0043
15:03 | 7.5374 | 7.34 | 0.1974 | 11:46 | 7.3192 | 7.351 | 0.0318 | 11:27 | 7.322 | 7.312 | 0.01
15:03 | 7.3472 | 7.375 | 0.0278 | 11:47 | 7.344 | 7.37 | 0.026 | 11:27 | 7.3037 | 7.299 | 0.0047
15:04 | 7.3548 | 7.322 | 0.0328 | 11:47 | 7.2915 | 7.377 | 0.0855 | 11:27 | 7.3086 | 7.3 | 0.0086
15:04 | 7.3684 | 7.296 | 0.0724 | 11:47 | 7.3586 | 7.397 | 0.0384 | 11:28 | 7.3038 | 7.301 | 0.0028
15:04 | 7.3224 | 7.291 | 0.0314 | 11:47 | 7.2854 | 7.377 | 0.0916 | 11:28 | 7.3296 | 7.32 | 0.0096
15:04 | 7.2912 | 7.284 | 0.0072 | 11:47 | 7.287 | 7.388 | 0.101 | 11:28 | 7.3596 | 7.36 | 0.0004
15:04 | 7.3051 | 7.368 | 0.0629 | 11:47 | 7.3578 | 7.437 | 0.0792 | 11:28 | 7.414 | 7.397 | 0.017
15:04 | 7.3993 | 7.301 | 0.0983 | 11:48 | 7.3831 | 7.465 | 0.0819 | 11:28 | 7.4308 | 7.421 | 0.0098
15:05 | 7.3197 | 7.255 | 0.0647 | 11:48 | 7.3979 | 7.482 | 0.0841 | 11:28 | 7.4314 | 7.42 | 0.0114
15:05 | 7.2755 | 7.226 | 0.0495 | 11:48 | 7.3911 | 7.479 | 0.0879 | 11:29 | 7.4059 | 7.402 | 0.0039
15:05 | 7.244 | 7.186 | 0.058 | 11:48 | 7.4312 | 7.456 | 0.0248 | 11:29 | 7.3794 | 7.372 | 0.0074
15:05 | 7.1959 | 7.188 | 0.0079 | 11:48 | 7.4315 | 7.445 | 0.0135 | 11:29 | 7.3394 | 7.335 | 0.0044
15:05 | 7.2296 | 7.194 | 0.0356 | 11:48 | 7.3262 | 7.39 | 0.0638 | 11:29 | 7.3147 | 7.309 | 0.0057
15:05 | 7.2202 | 7.222 | 0.0018 | 11:49 | 7.3203 | 7.331 | 0.0107 | 11:29 | 7.3067 | 7.29 | 0.0167
15:06 | 7.2625 | 7.313 | 0.0505 | 11:49 | 7.2305 | 7.305 | 0.0745 | 11:29 | 7.2898 | 7.285 | 0.0048
15:06 | 7.3318 | 7.271 | 0.0608 | 11:49 | 7.2512 | 7.299 | 0.0478 | 11:30 | 7.2731 | 7.271 | 0.0021
15:06 | 7.2838 | 7.221 | 0.0628 | 11:49 | 7.2746 | 7.29 | 0.0154 | 11:30 | 7.2639 | 7.247 | 0.0169
15:06 | 7.2258 | 7.207 | 0.0188 | 11:49 | 7.2587 | 7.297 | 0.0383 | 11:30 | 7.2276 | 7.222 | 0.0056
15:06 | 7.2055 | 7.188 | 0.0175 | 11:49 | 7.2825 | 7.293 | 0.0105 | 11:30 | 7.2146 | 7.209 | 0.0056
15:06 | 7.2483 | 7.228 | 0.0203 | 11:50 | 7.2833 | 7.287 | 0.0037 | 11:30 | 7.1982 | 7.199 | 0.0008
15:07 | 7.237 | 7.22 | 0.017 | 11:50 | 7.2608 | 7.267 | 0.0062 | 11:30 | 7.1852 | 7.183 | 0.0022
15:07 | 7.2879 | 7.254 | 0.0339 | 11:50 | 7.2645 | 7.283 | 0.0185 | 11:31 | 7.1938 | 7.193 | 0.0008
15:07 | 7.2689 | 7.279 | 0.0101 | 11:50 | 7.3001 | 7.306 | 0.0059 | 11:31 | 7.2515 | 7.233 | 0.0185
15:07 | 7.3245 | 7.294 | 0.0305 | 11:50 | 7.2928 | 7.308 | 0.0152 | 11:31 | 7.2855 | 7.294 | 0.0085
15:07 | 7.3015 | 7.334 | 0.0325 | 11:50 | 7.2884 | 7.338 | 0.0496 | 11:31 | 7.3266 | 7.316 | 0.0106
15:07 | 7.343 | 7.34 | 0.003 | 11:51 | 7.337 | 7.363 | 0.026 | 11:31 | 7.3194 | 7.307 | 0.0124
15:08 | 7.3312 | 7.268 | 0.0632 | 11:51 | 7.331 | 7.366 | 0.035 | 11:31 | 7.3003 | 7.303 | 0.0027
15:08 | 7.2931 | 7.269 | 0.0241 | 11:51 | 7.3015 | 7.352 | 0.0505 | 11:32 | 7.2596 | 7.271 | 0.0114
15:08 | 7.3173 | 7.316 | 0.0013 | 11:51 | 7.3466 | 7.353 | 0.0064 | 11:32 | 7.2776 | 7.27 | 0.0076
15:08 | 7.3474 | 7.357 | 0.0096 | 11:51 | 7.2466 | 7.336 | 0.0894 | 11:32 | 7.2706 | 7.269 | 0.0016
15:08 | 7.3795 | 7.364 | 0.0155 | 11:51 | 7.3101 | 7.309 | 0.0011 | 11:32 | 7.2788 | 7.275 | 0.0038
15:08 | 7.3842 | 7.391 | 0.0068 | 11:52 | 7.2718 | 7.277 | 0.0052 | 11:32 | 7.2727 | 7.27 | 0.0027
15:09 | 7.4576 | 7.488 | 0.0304 | 11:52 | 7.2502 | 7.317 | 0.0668 | 11:32 | 7.282 | 7.275 | 0.007
15:09 | 7.5202 | 7.41 | 0.1102 | 11:52 | 7.2892 | 7.303 | 0.0138 | 11:33 | 7.2544 | 7.253 | 0.0014
15:09 | 7.4203 | 7.356 | 0.0643 | 11:52 | 7.2562 | 7.321 | 0.0648 | 11:33 | 7.2397 | 7.218 | 0.0217
15:09 | 7.3463 | 7.317 | 0.0293 | 11:52 | 7.2328 | 7.329 | 0.0962 | 11:33 | 7.193 | 7.194 | 0.001
15:09 | 7.3422 | 7.324 | 0.0182 | 11:52 | 7.2049 | 7.304 | 0.0991 | 11:33 | 7.1839 | 7.178 | 0.0059
15:09 | 7.3484 | 7.351 | 0.0026 | 11:53 | 7.2351 | 7.298 | 0.0629 | 11:33 | 7.1906 | 7.188 | 0.0026
15:10 | 7.3719 | 7.403 | 0.0311 | 11:53 | 7.1941 | 7.291 | 0.0969 | 11:33 | 7.2013 | 7.207 | 0.0057
15:10 | 7.4383 | 7.481 | 0.0427 | 11:53 | 7.1843 | 7.256 | 0.0717 | 11:34 | 7.2255 | 7.245 | 0.0195
15:10 | 7.5004 | 7.515 | 0.0146 | 11:53 | 7.2423 | 7.28 | 0.0377 | 11:34 | 7.3096 | 7.3 | 0.0096
15:10 | 7.561 | 7.531 | 0.03 | 11:53 | 7.2566 | 7.288 | 0.0314 | 11:34 | 7.2967 | 7.291 | 0.0057
15:10 | 7.5467 | 7.546 | 0.0007 | 11:53 | 7.2372 | 7.312 | 0.0748 | 11:34 | 7.2915 | 7.287 | 0.0045
15:10 | 7.5635 | 7.501 | 0.0625 | 11:54 | 7.1922 | 7.306 | 0.1138 | 11:34 | 7.2801 | 7.272 | 0.0081
|  | Average | 0.038517 |  |  | Average | 0.041672 |  |  | Average | 0.007545
CHWR-1 Temperature (°C) |  |  |  | CHWR-2 Temperature (°C) |  |  |  | CHWR-3 Temperature (°C)
Time | BMS | FLUKE | ABS Diff | Time | BMS | FLUKE | ABS Diff | Time | BMS | FLUKE | ABS Diff
13:39 | 11.4436 | 11.429 | 0.0146 | 19:04 | 13.701 | 13.667 | 0.034 | 13:56 | 14.4977 | 14.508 | 0.0103
13:39 | 11.4346 | 11.421 | 0.0136 | 19:04 | 13.621 | 13.644 | 0.023 | 13:56 | 14.5381 | 14.514 | 0.0241
13:39 | 11.4383 | 11.423 | 0.0153 | 19:04 | 13.7412 | 13.78 | 0.0388 | 13:57 | 14.5665 | 14.532 | 0.0345
13:39 | 11.4307 | 11.409 | 0.0217 | 19:05 | 14.0291 | 14.039 | 0.0099 | 13:57 | 14.572 | 14.515 | 0.057
13:39 | 11.3904 | 11.384 | 0.0064 | 19:05 | 14.3512 | 14.322 | 0.0292 | 13:57 | 14.5227 | 14.494 | 0.0287
13:39 | 11.351 | 11.334 | 0.017 | 19:05 | 14.539 | 14.528 | 0.011 | 13:57 | 14.4476 | 14.399 | 0.0486
13:40 | 11.3295 | 11.308 | 0.0215 | 19:05 | 14.498 | 14.513 | 0.015 | 13:57 | 14.4274 | 14.397 | 0.0304
13:40 | 11.283 | 11.273 | 0.01 | 19:05 | 14.2415 | 14.281 | 0.0395 | 13:57 | 14.3543 | 14.417 | 0.0627
13:40 | 11.2682 | 11.257 | 0.0112 | 19:05 | 14.0621 | 14.074 | 0.0119 | 13:58 | 14.3906 | 14.395 | 0.0044
13:40 | 11.2502 | 11.239 | 0.0112 | 19:06 | 13.8532 | 13.883 | 0.0298 | 13:58 | 14.3874 | 14.351 | 0.0364
13:40 | 11.2353 | 11.224 | 0.0113 | 19:06 | 13.7714 | 13.741 | 0.0304 | 13:58 | 14.3937 | 14.394 | 0.0003
13:40 | 11.2611 | 11.247 | 0.0141 | 19:06 | 13.631 | 13.638 | 0.007 | 13:58 | 14.3804 | 14.354 | 0.0264
13:41 | 11.2707 | 11.256 | 0.0147 | 19:06 | 13.5763 | 13.61 | 0.0337 | 13:58 | 14.3706 | 14.316 | 0.0546
13:41 | 11.2754 | 11.275 | 0.0004 | 19:06 | 13.5582 | 13.553 | 0.0052 | 13:58 | 14.2643 | 14.29 | 0.0257
13:41 | 11.3199 | 11.306 | 0.0139 | 19:06 | 13.5439 | 13.535 | 0.0089 | 13:59 | 14.2604 | 14.306 | 0.0456
13:41 | 11.3242 | 11.314 | 0.0102 | 19:07 | 13.5224 | 13.498 | 0.0244 | 13:59 | 14.3334 | 14.27 | 0.0634
13:41 | 11.3555 | 11.342 | 0.0135 | 19:07 | 13.4621 | 13.473 | 0.0109 | 13:59 | 14.3315 | 14.308 | 0.0235
13:41 | 11.3687 | 11.353 | 0.0157 | 19:07 | 13.423 | 13.413 | 0.01 | 13:59 | 14.4569 | 14.377 | 0.0799
13:42 | 11.3863 | 11.371 | 0.0153 | 19:07 | 13.6231 | 13.653 | 0.0299 | 13:59 | 14.4404 | 14.425 | 0.0154
13:42 | 11.4036 | 11.384 | 0.0196 | 19:07 | 13.7254 | 13.716 | 0.0094 | 13:59 | 14.4041 | 14.417 | 0.0129
13:42 | 11.4 | 11.383 | 0.017 | 19:07 | 13.738 | 13.701 | 0.037 | 14:00 | 14.4228 | 14.376 | 0.0468
13:42 | 11.3731 | 11.363 | 0.0101 | 19:08 | 13.7435 | 13.713 | 0.0305 | 14:00 | 14.4511 | 14.402 | 0.0491
13:42 | 11.3628 | 11.345 | 0.0178 | 19:08 | 13.7204 | 13.725 | 0.0046 | 14:00 | 14.4229 | 14.442 | 0.0191
13:42 | 11.3357 | 11.323 | 0.0127 | 19:08 | 13.7497 | 13.716 | 0.0337 | 14:00 | 14.3982 | 14.408 | 0.0098
13:43 | 11.3257 | 11.315 | 0.0107 | 19:08 | 13.6958 | 13.733 | 0.0372 | 14:00 | 14.4399 | 14.43 | 0.0099
13:43 | 11.3007 | 11.285 | 0.0157 | 19:08 | 13.7492 | 13.719 | 0.0302 | 14:00 | 14.4454 | 14.429 | 0.0164
13:43 | 11.2322 | 11.222 | 0.0102 | 19:08 | 13.738 | 13.74 | 0.002 | 14:01 | 14.5135 | 14.406 | 0.1075
13:43 | 11.1925 | 11.172 | 0.0205 | 19:09 | 13.7451 | 13.716 | 0.0291 | 14:01 | 14.3845 | 14.434 | 0.0495
13:43 | 11.165 | 11.142 | 0.023 | 19:09 | 13.6962 | 13.678 | 0.0182 | 14:01 | 14.338 | 14.325 | 0.013
13:43 | 11.1196 | 11.11 | 0.0096 | 19:09 | 13.7216 | 13.707 | 0.0146 | 14:01 | 14.2797 | 14.219 | 0.0607
13:44 | 11.1266 | 11.114 | 0.0126 | 19:09 | 13.6172 | 13.651 | 0.0338 | 14:01 | 14.3006 | 14.266 | 0.0346
13:44 | 11.1209 | 11.109 | 0.0119 | 19:09 | 13.453 | 13.413 | 0.04 | 14:01 | 14.203 | 14.192 | 0.011
13:44 | 11.1376 | 11.125 | 0.0126 | 19:09 | 13.3061 | 13.344 | 0.0379 | 14:02 | 14.2721 | 14.251 | 0.0211
13:44 | 11.1438 | 11.129 | 0.0148 | 19:10 | 13.3136 | 13.326 | 0.0124 | 14:02 | 14.2908 | 14.342 | 0.0512
13:44 | 11.1314 | 11.118 | 0.0134 | 19:10 | 13.32 | 13.343 | 0.023
13:44 | 11.1045 | 11.089 | 0.0155 | 19:10 | 13.289 | 13.283 | 0.006
13:45 | 11.1059 | 11.091 | 0.0149 | 19:10 | 13.3059 | 13.265 | 0.0409
13:45 | 11.093 | 11.078 | 0.015 | 19:10 | 13.2314 | 13.266 | 0.0346
13:45 | 11.0799 | 11.071 | 0.0089 | 19:10 | 13.2797 | 13.288 | 0.0083
13:45 | 11.0602 | 11.05 | 0.0102 | 19:11 | 13.3216 | 13.305 | 0.0166
13:45 | 11.0586 | 11.041 | 0.0176 | 19:11 | 13.2475 | 13.251 | 0.0035
13:45 | 11.0677 | 11.055 | 0.0127 | 19:11 | 13.2621 | 13.228 | 0.0341
13:46 | 11.0858 | 11.073 | 0.0128 | 19:11 | 13.4403 | 13.428 | 0.0123
13:46 | 11.12 | 11.1 | 0.02 | 19:11 | 13.5481 | 13.511 | 0.0371
13:46 | 11.1743 | 11.157 | 0.0173 | 19:11 | 13.5023 | 13.517 | 0.0147
13:46 | 11.1889 | 11.177 | 0.0119 | 19:12 | 13.53 | 13.502 | 0.028
13:46 | 11.2025 | 11.189 | 0.0135 | 19:12 | 13.3863 | 13.402 | 0.0157
13:46 | 11.2192 | 11.211 | 0.0082 | 19:12 | 13.3491 | 13.382 | 0.0329
13:47 | 11.2415 | 11.229 | 0.0125 | 19:12 | 13.33 | 13.364 | 0.034
13:47 | 11.2633 | 11.253 | 0.0103 | 19:12 | 13.2912 | 13.326 | 0.0348
13:47 | 11.2919 | 11.276 | 0.0159 | 19:12 | 13.319 | 13.325 | 0.006
13:47 | 11.2954 | 11.282 | 0.0134 | 19:13 | 13.3102 | 13.303 | 0.0072
13:47 | 11.2802 | 11.268 | 0.0122 | 19:13 | 13.3266 | 13.293 | 0.0336
13:47 | 11.2135 | 11.211 | 0.0025 | 19:10 | 13.289 | 13.294 | 0.005
13:48 | 11.1875 | 11.167 | 0.0205 | 19:10 | 13.2319 | 13.26 | 0.0281
13:48 | 11.1467 | 11.125 | 0.0217 | 19:10 | 13.2314 | 13.266 | 0.0346
13:48 | 11.1016 | 11.09 | 0.0116 | 19:10 | 13.132 | 13.145 | 0.013
13:48 | 11.089 | 11.081 | 0.008 | 19:11 | 13.139 | 13.146 | 0.007
13:48 | 11.0904 | 11.078 | 0.0124 | 19:11 | 13.2025 | 13.168 | 0.0345
13:48 | 11.1178 | 11.107 | 0.0108 | 19:11 | 13.171 | 13.185 | 0.014
|  | Average | 0.013568 |  |  | Average | 0.02221 |  |  | Average | 0.034838
CWS Temperature (°C) |  |  |  | CWR Temperature (°C)
Time | BMS | FLUKE | ABS Diff | Time | BMS | FLUKE | ABS Diff
16:40 | 28.7127 | 28.702 | 0.0107 | 18:48 | 32.2502 | 32.253 | 0.0028
16:40 | 28.7205 | 28.717 | 0.0035 | 18:48 | 32.2596 | 32.255 | 0.0046
16:41 | 28.7233 | 28.716 | 0.0073 | 18:48 | 32.2538 | 32.262 | 0.0082
16:41 | 28.7124 | 28.712 | 0.0004 | 18:48 | 32.2657 | 32.257 | 0.0087
16:41 | 28.7065 | 28.702 | 0.0045 | 18:49 | 32.2592 | 32.259 | 0.0002
16:41 | 28.7018 | 28.698 | 0.0038 | 18:49 | 32.266 | 32.271 | 0.005
16:41 | 28.6994 | 28.696 | 0.0034 | 18:49 | 32.2704 | 32.275 | 0.0046
16:42 | 28.7009 | 28.7 | 0.0009 | 18:49 | 32.2794 | 32.281 | 0.0016
16:42 | 28.7208 | 28.716 | 0.0048 | 18:49 | 32.2784 | 32.279 | 0.0006
16:42 | 28.7296 | 28.729 | 0.0006 | 18:49 | 32.2672 | 32.266 | 0.0012
16:42 | 28.7377 | 28.725 | 0.0127 | 18:50 | 32.2633 | 32.261 | 0.0023
16:42 | 28.7448 | 28.732 | 0.0128 | 18:50 | 32.2509 | 32.252 | 0.0011
16:42 | 28.7459 | 28.741 | 0.0049 | 18:50 | 32.2318 | 32.245 | 0.0132
16:42 | 28.7337 | 28.737 | 0.0033 | 18:50 | 32.2501 | 32.261 | 0.0109
16:43 | 28.7224 | 28.721 | 0.0014 | 18:50 | 32.2895 | 32.284 | 0.0055
16:43 | 28.7197 | 28.722 | 0.0023 | 18:50 | 32.2912 | 32.294 | 0.0028
16:43 | 28.7218 | 28.718 | 0.0038 | 18:51 | 32.3136 | 32.307 | 0.0066
16:43 | 28.7219 | 28.72 | 0.0019 | 18:51 | 32.3083 | 32.305 | 0.0033
16:43 | 28.7237 | 28.717 | 0.0067 | 18:51 | 32.3041 | 32.306 | 0.0019
16:44 | 28.7044 | 28.71 | 0.0056 | 18:51 | 32.2892 | 32.29 | 0.0008
16:44 | 28.699 | 28.698 | 0.001 | 18:51 | 32.2584 | 32.264 | 0.0056
16:44 | 28.6888 | 28.694 | 0.0052 | 18:51 | 32.2328 | 32.238 | 0.0052
16:44 | 28.6833 | 28.682 | 0.0013 | 18:52 | 32.2287 | 32.235 | 0.0063
16:44 | 28.6784 | 28.682 | 0.0036 | 18:52 | 32.2275 | 32.232 | 0.0045
16:44 | 28.6766 | 28.679 | 0.0024 | 18:52 | 32.243 | 32.242 | 0.001
16:44 | 28.6869 | 28.682 | 0.0049 | 18:52 | 32.264 | 32.264 | 0
16:45 | 28.6783 | 28.679 | 0.0007 | 18:52 | 32.2572 | 32.272 | 0.0148
16:45 | 28.6645 | 28.666 | 0.0015 | 18:52 | 32.2993 | 32.293 | 0.0063
16:45 | 28.6702 | 28.669 | 0.0012 | 18:53 | 32.3029 | 32.312 | 0.0091
16:45 | 28.6724 | 28.672 | 0.0004 | 18:53 | 32.3304 | 32.329 | 0.0014
16:45 | 28.6861 | 28.68 | 0.0061 | 18:53 | 32.3342 | 32.332 | 0.0022
16:46 | 28.6673 | 28.674 | 0.0067 | 18:53 | 32.3545 | 32.349 | 0.0055
16:46 | 28.6539 | 28.658 | 0.0041 | 18:53 | 32.3453 | 32.346 | 0.0007
16:46 | 28.6592 | 28.659 | 0.0002 | 18:53 | 32.333 | 32.333 | 0
16:46 | 28.6685 | 28.664 | 0.0045 | 18:54 | 32.321 | 32.33 | 0.009
16:46 | 28.6521 | 28.654 | 0.0019 | 18:54 | 32.3322 | 32.33 | 0.0022
16:46 | 28.6365 | 28.64 | 0.0035 | 18:54 | 32.3262 | 32.325 | 0.0012
16:46 | 28.6379 | 28.637 | 0.0009 | 18:54 | 32.3296 | 32.328 | 0.0016
16:47 | 28.6354 | 28.637 | 0.0016 | 18:54 | 32.3461 | 32.339 | 0.0071
16:47 | 28.6395 | 28.64 | 0.0005 | 18:54 | 32.341 | 32.337 | 0.004
16:47 | 28.6233 | 28.628 | 0.0047 | 18:55 | 32.3684 | 32.358 | 0.0104
16:47 | 28.6243 | 28.63 | 0.0057 | 18:55 | 32.36 | 32.36 | 0
16:47 | 28.631 | 28.627 | 0.004 | 18:55 | 32.361 | 32.355 | 0.006
16:48 | 28.6318 | 28.628 | 0.0038 | 18:55 | 32.3525 | 32.348 | 0.0045
16:48 | 28.6495 | 28.643 | 0.0065 | 18:55 | 32.3633 | 32.353 | 0.0103
16:48 | 28.6586 | 28.651 | 0.0076 | 18:55 | 32.3632 | 32.362 | 0.0012
16:48 | 28.6729 | 28.659 | 0.0139 | 18:56 | 32.3571 | 32.354 | 0.0031
16:48 | 28.6682 | 28.666 | 0.0022 | 18:56 | 32.3731 | 32.364 | 0.0091
16:48 | 28.6517 | 28.656 | 0.0043 | 18:56 | 32.3716 | 32.372 | 0.0004
16:48 | 28.6651 | 28.663 | 0.0021 | 18:56 | 32.3759 | 32.376 | 0.0001
16:49 | 28.662 | 28.664 | 0.002 | 18:56 | 32.3723 | 32.374 | 0.0017
16:49 | 28.6587 | 28.661 | 0.0023 | 18:56 | 32.3875 | 32.384 | 0.0035
16:49 | 28.6597 | 28.661 | 0.0013 | 18:57 | 32.3793 | 32.382 | 0.0027
16:49 | 28.6695 | 28.663 | 0.0065 | 18:57 | 32.3661 | 32.369 | 0.0029
16:49 | 28.6749 | 28.668 | 0.0069 | 18:57 | 32.3638 | 32.367 | 0.0032
16:50 | 28.6724 | 28.671 | 0.0014 | 18:57 | 32.352 | 32.351 | 0.001
16:50 | 28.6667 | 28.667 | 0.0003 | 18:57 | 32.3476 | 32.354 | 0.0064
16:50 | 28.6666 | 28.666 | 0.0006 | 18:57 | 32.3524 | 32.335 | 0.0174
16:50 | 28.6691 | 28.661 | 0.0081 | 18:58 | 32.3359 | 32.331 | 0.0049
16:50 | 28.6739 | 28.67 | 0.0039 | 18:58 | 32.34 | 32.341 | 0.001
|  | Average | 0.0039267 |  |  | Average | 0.00439

## 4. Energy Consumption
Energy Use Intensity (3 Years Electricity Bill)
Energy Consumption (1st Year, Baseline)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'18 | 1428556 | 13401 | 1215155
Yearly Consumption | 1428556 | 13401 | 1215155
Energy Consumption (2nd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'19 | 1356746 | 9944 | 1086802
Yearly Consumption | 1356746 | 9944 | 1086802
Baseline Improvement | 5.027%
Energy Consumption (3rd Year)
Month | Total Consumption (kWh) | Tenant's Consumption (kWh) | Landlord's Consumption (kWh)
e.g. Jun'20 | 1273303 | 11049 | 1082254
Yearly Consumption | 1273303 | 11049 | 1082254
Baseline Improvement | 10.87%
Computation of Energy Use Intensity (EUI) based on area (kW/m²/year)
| Year 1 | Year 2 | Year 3
| Jun 2018 - May 2018 | Jun 2019 - May 2019 | Jun 2020 - May 2020
Total Building Energy Consumption (kWh) | 1428556 | 1356746 | 1273303
Gross Floor Area,m² (GFA) | 12500
Energy Use Intensity, EUI | 114.2845 | 108.5397 | 101.8642
Deviation | Baseline | -5.027% | -10.87%
Reasons, if deviation > ± 5% | - |  | Due to Covid, less people in offices. Replace to LED lightings in basement car park.

## 5. Water Consumption
Water Efficiency (3 Years Building Water Bill)
Water Consumption (1st Year, Baseline)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'18 | 12256.1 | 376 | 11880.1
Yearly Consumption | 12256.1 | 376 | 11880.1
Water Consumption (2nd Year)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'19 | 11682.2 | 603 | 11079.2
Yearly Consumption | 11682.2 | 603 | 11079.2
Baseline Improvement | 4.683%
Water Consumption (3rd Year)
Month | Total Consumption (m³) | Tenant's Consumption (m³) | Landlord's Consumption (m³)
e.g. Jun'20 | 11288.1 | 711 | 9977.1
Yearly Consumption | 11288.1 | 711 | 9977.1
Baseline Improvement | 7.898%
| Year 1 | Year 2 | Year 3
| Jun 2018 - May 2018 | Jun 2019 - May 2019 | Jun 2020 - May 2020
Total Building Water Consumption (m3) | 12256.1 | 11682.2 | 11288.1
Deviation | Baseline | -4.683% | -7.898%
Reasons, if deviation > ± 5% | - |  | Due to Covid, less people in offices.

## 6. Energy & Water Improve Plan
Energy and Water Improvement Plan
Submission of plans showing intent, measures and implementation strategies to achieve improvement target set against current performance over the next 3 years.
3 Years Energy Efficiency Improvement Target: | % | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
3 Years Water Efficiency Improvement Target: | % | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Click to attach Energy Improvement Plan
Click to attach Water Improvement Plan

## 7. CoC
Cycles of Concentration (for water-cooled chiller plant only)
Submission of cooling tower’s water treatment reports showing 7 or better cycles of concentration.
Cycle of Concentration: |  | Cycles | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Cooling Tower water analysis report
Month | COC
Average
Click to attach Water Treatment Report

## 8. Sustainable OM (hidden)
Sustainable Operations & Management
Occupant Satisfaction Survey
A post-occupancy evaluation is a survey to gauge occupants’ satisfaction on indoor environmental quality and identify corrective actions that will enhance comfort. Please ask your assessor for a survey weblink for this project, which may then be disseminated to occupants. Results will be tabulated automatically, so that FM may view them and record corrective actions taken. Alternatively, you may use the attached questionaire from Annex B of GM ENRB:2017, and tabulate the response with the attached result template. | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Environmental Policy
Environmental Policy that reflects sustainability goals set for the building and its systems | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Waste Recycling Reports
Name of waste recycling company: | Use "Insert..Object..Create from File" command if macro execution is disabled
Assessor's comment:
Click to attach Occupant Satisfaction Result
Click to attach Environment Policy Statement
Clcik to attach Waste Recycling Reports
Click to attach scanned images of completed survey forms

## 8. IEQ
Indoor Environment Quality
IAQ Audit
Submission of latest IAQ audit report performed by accredited consultants/companies, stating major areas of concern (e.g. mold issues).
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Date Audit was Conducted:
Name of SAC-Accredited Lab:
Assessor's comment:
Lighting Lux Level
Submission of lighting lux levels for various areas, complying with SS531 or CP38.
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Measurements taken by:
Assessor's comment:
Noise Level
Submission of noise levels for internal areas, complying with SS553 or CP13.
Test Report Number: | Use "Insert..Object..Create from File" command if macro execution is disabled
Measurements taken by:
Assessor's comment:
Click to attach IAQ Audit Report
Click to attach Lux Level Reading
Click to attach Noise Level Reading

## 9. Others
OTHERS
POE survey
Submit POE survey results done with past one (1) year
Date/Period POE survey done
No. of occupants in the building
No. of respondents
Assessor's comment:
Waste reports
Submit past one year's waste collection report detailing the breakdown of types and quantity of recyclables and non-recyclables
Types of recyclables
Assessor's comment:
Tenants/Occupants engagement
Submit photos of sustainability or health and wellbeing related activities organised by Green Building Committee or building management. At least 3 activities per year.
1st activity | e.g. Earth hour
2nd activity | e.g. Exhibition in Atrium on Global Warming
3rd activity
Assessor's comment:
Click to attach waste reports of recycles and non-recycles
Click to attach photos of activities
Click to attach POE survey results

## Sheet1 (hidden)
1 | Energy and water consumption for past three years
2 | IAQ audit
3 | POE
4 | Lux level measurement
5 | Smart control (co2) for refresh air intake
6 | Lighting control (occupancy sensors)
7 | monitoring recycles and non-recycles
8 | energy and water improvement plan
9 | at least 3 green or health related activities for tenants per year