## General Info
General Information
Building Name | e.g. Building ABC
Building Address | e.g. Blk 25 Jurong Street Singapore 123456
Building Type | e.g Mix development (Hotel/Retail)
PE(Mech) | e.g Vince Tan
PE(Mech) Address | e.g blk 22 Bishan Street, #04-15, Singapore 654321
Chiller Configuration | e.g 2 x 550RT, 1 x 300RT
Operating Cooling Load | e.g 810 RT
Design Chilled Water Supply Temperature | e.g 6.67 °C
Design Chilled Water Delta T | e.g 5.5°C
Design Condenser Supply Water Temperature | e.g 29.7°C
Design Condenser Delta T | FIX/VARIABLE <please choose one>
Design Chilled Water Flow Rate | e.g 60 L/s
Design Condenser Water Flow Rate | e.g 70 L/s

## Chiller(s)
| % Load | CHILLER 1 | [8 empty] | % Load | CHILLER 2
|  | Capacity (RT) | Chiller Input Power (kW) | Chiller Efficiency kW/RT | Evaporator |  |  | Condenser |  |  |  | Capacity (RT) | Chiller Input Power (kW) | Chiller Efficiency kW/RT | Evaporator |  |  | Condenser
[5 empty] | Flow (L/s) | CHWST (°C) | CHWRT (°C) | Flow (L/s) | CWST (°C) | CWRT (°C) |  |  |  |  | Flow (L/s) | CHWST (°C) | CHWRT (°C) | Flow (L/s) | CWST (°C) | CWRT (°C)
example | 100 | 700 | 363 | 0.519 | 106 | 6.67 | 12.22 | 132 | 29.44 | 34.53 | 100 | 700
example | 90 | 630 | 329 | 0.52222 | 95.4072 | 6.67 | 12.22 | 119.259 | 29.44 | 34.53 | 90 | 630
| 80 | 560 | [8 empty] | 80 | 560
| 70 | 490 | [8 empty] | 70 | 490
| 60 | 420 | [8 empty] | 60 | 420
| 50 | 350 | [8 empty] | 50 | 350
| 40 | 280 | [8 empty] | 40 | 280
| 30 | 210 | [8 empty] | 30 | 210
| 20 | 140 | [8 empty] | 20 | 140
| 10 | 70 | [8 empty] | 10 | 70
| % Load | CHILLER 3 | [8 empty] | % Load | CHILLER 4
|  | Capacity (RT) | Chiller Input Power (kW) | Chiller Efficiency kW/RT | Evaporator |  |  | Condenser |  |  |  | Capacity (RT) | Chiller Input Power (kW) | Chiller Efficiency kW/RT | Evaporator |  |  | Condenser
[5 empty] | Flow (L/s) | CHWST (°C) | CHWRT (°C) | Flow (L/s) | CWST (°C) | CWRT (°C) |  |  |  |  | Flow (L/s) | CHWST (°C) | CHWRT (°C) | Flow (L/s) | CWST (°C) | CWRT (°C)
| 100 | 500 | [8 empty] | 100 | 500
| 90 | 450 | [8 empty] | 90 | 450
| 80 | 400 | [8 empty] | 80 | 400
| 70 | 350 | [8 empty] | 70 | 350
| 60 | 300 | [8 empty] | 60 | 300
| 50 | 250 | [8 empty] | 50 | 250
| 40 | 200 | [8 empty] | 40 | 200
| 30 | 150 | [8 empty] | 30 | 150
| 20 | 100 | [8 empty] | 20 | 100
| 10 | 50 | [8 empty] | 10 | 50

## Chilled Water Pump(s)
| % Load | Chilled Water Pump 1 |  |  |  |  | % Load | Chilled Water Pump 2
|  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D) |  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D)
|  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW) |  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW)
example | 100 | 106.01 | 28 | 90 | 80 | 40.4428 | 100
| 90 | 95.409 | 22.68 | 94.2 | 86.8 | 25.9616 | 90
| 80 | 84.808 | 17.92 | 90 | 80 | 20.7067 | 80
| 70 | 74.207 | 13.72 | 90 | 80 | 13.8719 | 70
| 60 | 63.606 | 10.08 | 90 | 80 | 8.7356 | 60
| 50 | N.A. | N.A. | N.A. | N.A. | N.A. | 50 | N.A. | N.A. | N.A. | N.A. | N.A.
| 40 | N.A. | N.A. | N.A. | N.A. | N.A. | 40 | N.A. | N.A. | N.A. | N.A. | N.A.
| 30 | N.A. | N.A. | N.A. | N.A. | N.A. | 30 | N.A. | N.A. | N.A. | N.A. | N.A.
| 20 | N.A. | N.A. | N.A. | N.A. | N.A. | 20 | N.A. | N.A. | N.A. | N.A. | N.A.
| 10 | N.A. | N.A. | N.A. | N.A. | N.A. | 10 | N.A. | N.A. | N.A. | N.A. | N.A.
| % Load | Chilled Water Pump 3 |  |  |  |  | % Load | Chilled Water Pump 4
|  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D) |  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D)
|  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW) |  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW)
| 100 | [5 empty] | 100
| 90 | [5 empty] | 90
| 80 | [5 empty] | 80
| 70 | [5 empty] | 70
| 60 | [5 empty] | 60
| 50 | N.A. | N.A. | N.A. | N.A. | N.A. | 50 | N.A. | N.A. | N.A. | N.A. | N.A.
| 40 | N.A. | N.A. | N.A. | N.A. | N.A. | 40 | N.A. | N.A. | N.A. | N.A. | N.A.
| 30 | N.A. | N.A. | N.A. | N.A. | N.A. | 30 | N.A. | N.A. | N.A. | N.A. | N.A.
| 20 | N.A. | N.A. | N.A. | N.A. | N.A. | 20 | N.A. | N.A. | N.A. | N.A. | N.A.
| 10 | N.A. | N.A. | N.A. | N.A. | N.A. | 10 | N.A. | N.A. | N.A. | N.A. | N.A.

## Condenser Water Pump(s)
| % Load | Condenser Water Pump 1 |  |  |  |  | % Load | Condenser Water Pump 2
|  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D) |  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D)
|  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW) |  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW)
example | 100 | 132.51 | 32 | 90 | 80 | 57.7744 | 100
| 90 | 119.259 | 25.92 | 90 | 80 | 42.1175 | 90
| 80 | 106.008 | 20.48 | 90 | 80 | 29.5805 | 80
| 70 | 92.757 | 15.68 | 90 | 80 | 19.8166 | 70
| 60 | 79.506 | 11.52 | 90 | 80 | 12.4793 | 60
| 50 | N.A. | N.A. | N.A. | N.A. | N.A. | 50 | N.A. | N.A. | N.A. | N.A. | N.A.
| 40 | N.A. | N.A. | N.A. | N.A. | N.A. | 40 | N.A. | N.A. | N.A. | N.A. | N.A.
| 30 | N.A. | N.A. | N.A. | N.A. | N.A. | 30 | N.A. | N.A. | N.A. | N.A. | N.A.
| 20 | N.A. | N.A. | N.A. | N.A. | N.A. | 20 | N.A. | N.A. | N.A. | N.A. | N.A.
| 10 | N.A. | N.A. | N.A. | N.A. | N.A. | 10 | N.A. | N.A. | N.A. | N.A. | N.A.
| % Load | Condenser Water Pump 3 |  |  |  |  | % Load | Condenser Water Pump 4
|  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D) |  | A | B | C | D | E = (A x 1000 x 9.81 x B) / (106 x C x D)
|  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW) |  | Rated Flow (L/s) | Rated Head (m) | Motor Efficiency (%) | Pump Efficiency (%) | Motor Absorbed Power (kW)
| 100 | [5 empty] | 100
| 90 | [5 empty] | 90
| 80 | [5 empty] | 80
| 70 | [5 empty] | 70
| 60 | [5 empty] | 60
| 50 | N.A. | N.A. | N.A. | N.A. | N.A. | 50 | N.A. | N.A. | N.A. | N.A. | N.A.
| 40 | N.A. | N.A. | N.A. | N.A. | N.A. | 40 | N.A. | N.A. | N.A. | N.A. | N.A.
| 30 | N.A. | N.A. | N.A. | N.A. | N.A. | 30 | N.A. | N.A. | N.A. | N.A. | N.A.
| 20 | N.A. | N.A. | N.A. | N.A. | N.A. | 20 | N.A. | N.A. | N.A. | N.A. | N.A.
| 10 | N.A. | N.A. | N.A. | N.A. | N.A. | 10 | N.A. | N.A. | N.A. | N.A. | N.A.

## Cooling Tower(s)
Cooling Towers
* Based on an ambient DBT 32 °C WBT of 27.5°C
Parameters | Cooling Tower 1 | Cooling Tower 2 | Cooling Tower 3 | Forced-draft, blow-thru type
Tower Capacity (RT) | 203.7037 | 203.2983 | 203.2983
Tower Capacity (kW) | 715 | 715 | 715
Number of Fan | 1 | 1 | 1
Airflow Rate (m3/min) | 1164 | 1164 | 1164
Absorbed Fan Power (kW) | 10.82 | 10.82 | 10.82 | Motor power rating = 15 kW
Total Each Fan Power (kW) | 10.82 | 10.82 | 10.82
Cooling Tower (Peak Load) - For 341RT chillers Operating CT1 + CT2 | Percentage of Load
| 100% (407 RT) | 90% (366RT) | 80% (326RT)
Total Capacity (kW) | 1430 | 1430 | 1430
Heat Rejected Load Requred (kW) | 1394.349 | 1249.49 | 1107.288
Number of Tower Operating | 2 | 2 | 2
Total Full Fan Power (kW) | 21.64 | 24.0444 | 27.05 | In the absent of detail data, assume fan efficiency drops accordingly to % Load.
Required Capacity for Each Tower | 97.51% | 87.38% | 77.43%
Total Airflow Rate (m3/min) | 2328 | 2328 | 2328
Required Airflow Rate (m3/min) | 2269.9612 | 2034.1348 | 1802.6339
Total Fan Power Required (kW) | 20.3164 | 17.1596 | 14.2718 | Provision of VSD set at min of 60% speed

## Total System Efficiency
|  |  | Chiller Plant System | [9 empty] | Air-Distribution System
|  | A | B | C | D | E | F | G | H | I | J = C + E + G + I | J/A
| Time | Cooling Load RT | Operating chiller(s) | Chiller(s) power input (kW) | Operating Chilled Water Pump(s) | Chilled water pump(s) power input (kW) | Operating Condenser Water Pump(s) | Condenser water pump(s) power input (kW) | Operating Cooling Tower(s) | Cooling Tower(s) power input (kW) | Total Chiller Plant Power Input (kW) | Chiller Plant Efficiency | Total CAV AHU Motor Input Power (kW) | *Total VAV AHU Motor Input Power (kW) | *Total FCU Motor Nameplate/Input Power (kW) | Total Air-side Motor Input Power (kW) | Air Distribution System Efficiency (kW/RT) | Air Distribution Configuration (FCU, PAU, AHU-VAV, AHU-CAV, e.t.c.) | Total Power Input of A/C System, Water+Air (kW) | Total Efficiency Water+Air (kW/RT)
| 0000 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0100 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0200 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0300 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0400 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0500 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0600 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0700 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 0800 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
example | 0900 | 1200 | 700 RT x 2 x 90% | 626.6667 | 45kW x 2 x 90% | 51.9231 | 55kW x 2 x 90% | 84.235 | 22.5kW x 3 | 14.58 | 777.4048 | 0.64784 | 61.22 | 28.125 | 1.25 | 90.595 | 0.075496 | e.g. 4 AHU-CAV, 10 AHU-VAV, 5 FCUs running at this hour | 867.9998 | 0.72333
| 1000 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1100 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1200 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1300 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1400 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1500 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1600 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1700 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1800 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 1900 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 2000 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 2100 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 2200 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
| 2300 | [9 empty] | 0 | #DIV/0! |  |  |  | 0 | #DIV/0! |  | 0 | #DIV/0!
Total
|  | A: RTH; Chiller Plant System C: kWH; Chiller Plant System E: kWH; Chiller Plant System G: kWH; Chiller Plant System I: kWH | kWH | kWH/RTH | kWH | kWH | kWH | kWH | kWH/RTH |  | kWH | kWH/RTH
| Individual equipment efficiency (kW/RT) = | Chiller Plant System C: #DIV/0!; Chiller Plant System E: #DIV/0!; Chiller Plant System G: #DIV/0!; Chiller Plant System I: #DIV/0! |  | #DIV/0!
*Note: The total hourly motor input power is based on aggregate of all constant or variable flow fans operating at this hour.
For Variable Fan flow, Part load fan power calculator may be referenced from ASHRAE 90.1, Table G3.1.3.15, Part-Load Perforamnce for VAV Fan Systems or Part-Load Fan Power Equation can be applied