## Summary
EXISTING NON-RESIDENTIAL BUILDINGS (GM ENRB: 2017)
GM Ref No |  |  |  | COMPLY
Building Name
Building Type
GFA (m2)
PRE-REQUISITE REQUIREMENTS FOR EXISTING NON-RESIDENTIAL BUILDING CRITERIA |  | CERTIFIED | GOLD | GOLDPLUS | PLATINUM
1 | Energy Consumption Monitoring
2 | Air Conditioning System Operating Efficiency |  |  |  |  | Office
3 | Energy Improvement on Lighting System |  |  |  |  | Retail
4 | Water Consumption Monitoring |  |  |  |  | Institution
5 | Chiller Plant Measurement and Verification (M&V) Instrumentation |  |  |  |  | Industrial
6 | Indoor Temperature |  |  |  |  | Mixed Used Development
7 | Indoor Air Quality (IAQ) Surveillance Audit |  |  |  |  | Hotel
8 | Tenant and Occupant Engagement |  |  |  |  | Serviced Apartment
9 | Recycling Facilities |  |  |  |  | Others
10 | Post Occupany Evaluation
11 | Display of Green Mark Plaque / Decal
Section |  | POINTS AVAILABLE | POINTS SCORED
1 | Sustainable Management | 35 | 0
2 | Building Energy Performance | 40 | 0
3 | Resource Stewardship | 30 | 0
4 | Smart and Healthy Building | 40 | 0
5 | Advanced Green Effort | 20 | 2
| Total | 165 | 2
SECTION 1 - SUSTAINABLE MANAGEMENT |  | POINTS AVAILABLE | POINTS SCORED
1.1 | Environmental Credentials of Facility Managers and Consultants | 1 | 0
1.2 | Sustainable Policy and Action Plan | 4 | 0
1.3 | Green Building Committee | 2 | 0
1.4 | Green Education | 2 | 0
1.5 | Green Fit-out Guidelines | 1 | 0
1.6 | Green Lease | 2 | 0
1.7 | Green-related Activities for Building Occupants | 3 | 0
1.8 | Greenery | 6 | 0
1.9 | Refrigerant | 4 | 0
1.10 | Green Transport | 4 | 0
1.11 | Sustainable Operation | 6 | 0
| Score for Section 1 - Sustainable Management | 35 | 0
SECTION 2 - BUILDING ENERGY PERFORMANCE
2.1 | Façade Performance | 2 | 0
2.2 | Air Conditioning System Operating Efficiency | 16 | 0
2.3 | Natural / Mechanical Ventilation Performance | 17 | 0
2.4 | Lighting System Efficiency | 6 | 0
2.5 | Vertical Transportation System | 1.5 | 0
2.6 | Ventilation in Car Park | 2 | 0
2.7 | Ventilation in Common Areas | 3 | 0
2.8 | Energy Efficient Practices and Features | 2 | 0
2.9 | Renewable Energy | 6.5 | 0
| Score for Section 2 - Building Energy Performance | 40 | 0
SECTION 3 - RESOURCE STEWARDSHIP
3.1 | Water Efficient Fittings | 7 | 0
3.2 | Landscape Irrigation | 1 | 0
3.3 | Reduction in Water Consumption of Cooling Towers | 2.5 | 0
3.4 | Water Monitoring and Leak Detection | 1 | 0
3.5 | Water Usage Portal and Dashboard | 1 | 0
3.6 | Use of Alternative Water Sources | 2 | 0
3.7 | Green Products and Materials | 7 | 0
3.8 | Recycling Facilities | 3.5 | 0
3.9 | Storage Area for Recyclable Waste | 1 | 0
3.10 | Promotion of Waste Reduction | 2 | 0
3.11 | Waste Monitoring | 2 | 0
| Score for Section 3 - Resource Stewardship | 30 | 0
SECTION 4 - SMART AND HEALTHY BUILDINGS
4.1 | Occupant Comfort | 5.5 | 0
4.2 | Outdoor Air Control | 1.5 | 0
4.3 | Enhanced Filtration Media | 2.5 | 0
4.4 | Indoor Contaminants | 2.5 | 0
4.5 | Lighting Quality | 4 | 0
4.6 | Acoustics | 1 | 0
4.7 | Biophilic Features | 2 | 0
4.8 | Energy Monitoring | 11 | 0
4.9 | Demand Control | 5 | 0
4.10 | Integration and Analytics | 5 | 0
| Score for Section 4 - Smart and Healthy Buildings | 40 | 0
SECTION 5 - ADVANCED GREEN EFFORT
| Advanced Green Effort | 20 | 2
| Score for Section 5 - Advanced Green Effort | 20 | 2

## Section 1
SECTION 1 - SUSTAINABLE MANAGEMENT |  | POINT SCORED | 0
PRE-REQUISITES |  | COMPLY
8 | TENANT AND OCCUPANT ENGAGEMENT | [8 empty] | FALSE | 0
1.1 | Environmental Credentials of Facility Managers and Consultants | DATA INPUT | AVAILABLE POINTS | POINT SCORED | REMARK
| To recognise facility managers, consultants with specialised green credentials who can effectively operate and/or guide the maintenance team towards sustainable management of the building. |  | 1 | 0
| a) Certified Green Mark AP (FM)/ GMFM | [8 empty] | FALSE | 0
| b) Certified Green Mark AAP (FM)/ GMFP | [8 empty] | FALSE | 0
| c) Singapore Certified Energy Manager (SCEM) | [8 empty] | FALSE | 0
1.2 | Sustainable Policy and Action Plan
| To recognise management's commitment and leadership towards sustainable operation and maintenace of the building. |  | 4 | 0
| a) Energy Management Policy and Energy Improvement Plan | [8 empty] | FALSE | 0
| b) Water Management Policy and Water Improvement Plan | [8 empty] | FALSE | 0
| c) Waste Management Policy and Waste Recycling Plan | [8 empty] | FALSE | 0
| d) Valid ISO 14001 or ISO 50001 Certifications | [8 empty] | FALSE | 0
1.3 | Green Building Committee
| To encourage collaborations between environmentally - conscious owners and tenants to promote sustainabiliity-related initiatives for the building. |  | 2 | 0
| a) Involve at least 3 tenants or building occupants | [8 empty] | FALSE | 0
| b) Involve at least 6 tenants or building occupants; and they represent more than 30% of total lettable area | [8 empty] | FALSE | 0
1.4 | Green Education
| To educate building users and tenants on the green features of the building and how they can contribute towards sustainability. |  | 2 | 0
| a) Green Building User Guide | [8 empty] | FALSE | 0
| b) Green Corner | [8 empty] | FALSE | 0
1.5 | Green Fit-out Guidelines
| Provision of Green Fit-out Guidelines. The guidelines are to be disseminated to the relevant tenant management and personnel. |  | 1 | 0 | [5 empty] | FALSE | 0
1.6 | Green Lease
| The green lease, to be incorporated into tenancy agreement shall establish agreed levels of environmental building performance between landlord and his tenants. |  | 2 | 0 | [5 empty] | FALSE | 0
| Total Net Lettable Area (m2) | [8 empty] | 0 | 0
| Net Lettable Area on Green Lease (m2) | [9 empty] | 0
| % Net Lettable Area on Green Lease | 0
1.7 | Green-related Activities for Building Occupants
| To encourage tenant and building occupant engagement through green or occupant well-being related activities. Points can be scored based on the number of activities held in a year. |  | 3 | 0
Number of activities held in a year
1.8 | Greenery
To provide greenergy within the development to reduce urban heat island effect.
a) | Greenery Provision |  | 2.5 | 0
GnP
b) | Rooftop Greenery |  | 1 | 0
[10 empty] | 0 | 0
Total roof area (m2)
Total green roof area (m2)
c) | Vertical Greenery |  | 1 | 0
Total verticial greenery area (m2)
d) | Sustainable Landscape Management |  | 1.5 | 0
| (i) Building landscape is certified under Nparks' Lanscape Excellence Assessment Framework (LEAF) | [8 empty] | FALSE | 0
| (ii) Adoption of the following landscape management plan | [9 empty] | 0
| a) Use of organice composts from horticultural wastes | [8 empty] | FALSE | 0
| b) Provision of onsite composting | [8 empty] | FALSE | 0
| c) Provision of general landscape maintenance and management plan | [8 empty] | FALSE | 0
1.9 | Refrigerant
To encourage the responsible use and management of environment-friendly refrigerants and to minimise the impact of refrigerants on the environment.
a) | Use of Green Refrigerant | [8 empty] | TRUE | 1
|  |  | 1.5 | 0
| Name of Green Refrigerant |  |  |  |  | 1 |  | 0 | 0 | 0 |  | 0
| ODP = 0 | [6 empty] | 0 |  | 0 |  | FALSE | 0
| GWP | [5 empty] | 0 | 0 | 0 | 0 |  | FALSE | 0 | 0
b) | Refrigerant leak detection system | [5 empty] | 0
| Provision of automated refrigerant leak detection system with detection points at critical areas in the plant room housing the chillers and/or equipment that contain refirigerants. |  | 1 | 0 | [5 empty] | FALSE | 0
c) | Refrigerant Management System
| A refrigerant management procedure or strategies are in place on proper handling of refrigerant during storage and top-up, maintaing of the log sheets, tracking and reducing the refrigerant consumption as well as avoiding leakages. |  | 1.5 | 0 | [5 empty] | FALSE | 0
1.1 | Green Transport
To encourage the use of alternative transportation modes such as public transport or cycling.
| a) Good access (<500m walking distance) to public transport networks such as MRT/ LRT stations and bus stops |  | 0.5 | 0 | [5 empty] | FALSE | 0
| b) Provision of covered walkway(s) to the nearest public transport networks |  | 0.5 | 0 | [5 empty] | FALSE | 0
| c) Provision of priority parking lots for hybrid and electric vehicle |  | 1.5 | 0 | [5 empty] | 0
| Total number of parking lots | [8 empty] | 0
Total number of priority parking lots
| Number of electric vehicle charging point near to the priority parking lots | [8 empty] | 0 | 0
| Provision of electrical vehicle charging and parking infrastructure for vehicles or to facilitate electric car-sharing services | [8 empty] | FALSE | 0
| d) Provision of bicycle parking lots, shower and changing facilities |  | 1.5 | 0 | [7 empty] | 0 | 0.5
| Gross Floor Area (m2) | 0
| Number of bicycle parking lots | [10 empty] | 0 | 1
| Provision of shower and changing facilities | [8 empty] | FALSE | 0 |  | 0
1.11 | Sustainable Operation
To implement various policies and measures to promote sustainable operations and maintenance within the building
a) | Provision of Green Procurement Policy, endorsed by the top management, on procuring green products, materials, goods and services from contractors and vendors committed to environmental sustainability |  | 1 | 0 | [5 empty] | FALSE | 0
b) | Performance-based Procurement for Retrofitting |  | 2 | 0
| (i) Centralised chilled-water system with guaranteed efficiency of 0.65 kW/RT or better | [8 empty] | FALSE | 0
| (ii) Air distribution system with guaranteed efficiency of 0.25kW/RT or better | [8 empty] | FALSE | 0
Guaranteed efficiency for chilled water system (kW/RT)
Guaranteed efficiency for air distribution system (kW/RT)
c) | Performance-based Procurement for Maintenance |  | 2 | 0
| (i) Centralised chilled-water system with guaranteed efficiency of 0.65 kW/RT or better | [8 empty] | FALSE | 0
| (ii) Air distribution system with guaranteed efficiency of 0.25kW/RT or better | [8 empty] | FALSE | 0
Guaranteed efficiency for chilled water system (kW/RT)
Guaranteed efficiency for air distribution system (kW/RT)
d) | System Handover and Documentation
| To maintain proper and updated system verification and handover documents of retrofitted building systems, including description of systems' operation and controls, testing and commissioning reports, as-built drawings, technical and training manuals and user guides |  | 1 | 0 | [5 empty] | FALSE | 0

## Section 2
SECTION 2 - BUILDING ENERGY PERFORMANCE |  | POINTS SCORED | 0
PRE-REQUISITES |  | COMPLY
1 | ENERGY CONSUMPTION MONITORING | [7 empty] | FALSE | 0
2 | AIR CONDITIONING SYSTEM MINIMUM OPERATING EFFICIENCY | [7 empty] | FALSE | 0
3 | ENERGY IMPROVEMENT ON LIGHTING SYSTEM | [7 empty] | FALSE | 0
5 | CHILLER PLANT MEASUREMENT AND VERIFICATION (M&V) INSTRUMENTATION | [7 empty] | FALSE | 0
2.1 | Façade Performance | DATA INPUT | AVAILABLE POINTS | POINT SCORED | REMARKS
| To enhance the overall thermal performance of the building envelope thus reducing the overall heat gain into the building. |  | 2 | 0
Envelope Thermal Transfer Value (ETTV) (W/m2)
2.2 | Air Conditioning System Operating Efficiency | [11 empty] | Water-cooled Chilled-water Plant
| Total Gross Floor Area (m2) | 0 | [10 empty] | Air-cooled Chilled-water Plant / Unitary Air-conditioners/ VRF with Permanent M&V
| Total Air-Condtioned Area (m2) | [11 empty] | Air-cooled Chilled-water Plant / Unitary Air-conditioners/ VRF without Permanent M&V
|  |  | 12 | 0 |  | 8 | 0 | 0 |  | 0 |  |  | District Cooling System
| Type of air-conditioning system (Primary) | [7 empty] | 1
System 1 Cooling Load (RT)
| Air Conditioning System Efficiency (kW/RT) |  |  |  |  | 8
| Other type of air-conditioning system | [5 empty] | 0 |  | 1
System 2 Cooling Load (RT)
| Air Conditioning System Efficiency (kW/RT) | [7 empty] | FALSE
| Air Distribution System |  | 4 | 0
Air distribution operating system efficiency baseline: 0.28 kW/RT
Air distribution operating system efficiency
EUIAC(kWh/m2·yr)
EUIAC# (kWh/m2·yr)
| % Improvement from baseline | 0 | [6 empty] | 0 | 100 | 0
2.3 | Natural/ Mechanical Ventilation Performance
| Applicable to non air-conditioned buildings, with an aggregate non air-conditioned building area > 10% of the total floor area excluding car parks and common areas. |  | 17 | 0
| Total Gross Floor Area (m2) | 0
Total Area with Natural Ventilation
Total Area with Mechanical Ventilation
| Total Non Air-Condtioned Area (m2) | 0
| % of Occupied Non Air-Conditioned Area | 0
a) | Natural Ventilation (only applicable to occupied areas, excluding circulation, plant rooms and transit areas)
| Use of natural ventilation | [7 empty] | FALSE | 0
| % of natural ventilated areas with window openings facing north and south directions and cross ventilation demonstrated | [7 empty] | 0
b) | Mechanical Ventilation | [6 empty] | 0
| To encourage the use of energy efficient mechanical ventilation system as the preferred ventilation mode to reduce the use of air-conditioning in buildings. | [7 empty] | 0
Efficiency of Mechanical Ventilation (W/CMH)
% Improvement from baseline
2.4 | Lighting System Efficiency
| To encourage the use of energy efficient lighting to minimise energy consumption from lighting usage while maintaining proper lighting level |  | 6 | 0
| % improvement from lighting power budget baseline in common area | [7 empty] | 0
| % improvement from lighting power budget baseline in lettable/ non-common area | [7 empty] | 0
2.5 | Verticial Transportation System
| To encourage the use of energy efficient vertical transportation systems within the building |  | 1.5 | 0
| a) Provision of lifts, escalators and travelators equipped with AC variable voltage and variable frequency (VVVF) motor drive and sleep mode features | [7 empty] | FALSE | 0
| b) Provision of lift with regenerative drive | [7 empty] | FALSE | 0
2.6 | Ventilation in Car Park |  | 2 | 0
To encourage the use of natural ventilation or energy efficient design and control of ventilation systems in carparks.
| a) Mechanically ventilated car parks with carbon monoxide (CO) sensor control | [7 empty] | FALSE | 0
| b) Carparks with natural ventilation /No carpark | [7 empty] | FALSE | 0
| c) Carpark with both natural and mechanical ventilation (CO sensor) | [7 empty] | FALSE | 0
Carpark area with natural ventilation (m2)
Carpark area with mechanical ventilation (m2)
2.7 | Ventilation in Common Areas | [11 empty] | 0
| To encourage the use of energy efficient ventilation systems in common areas as follows: |  | 3 | 0 | [6 empty] | 0 |  | 0
| i) Toilets | [7 empty] | FALSE | FALSE | 0 | 0 | 0
| ii) Staircases | [7 empty] | FALSE | FALSE | 0 | 0 | 0
| iii) Corridors | [7 empty] | FALSE | FALSE | 0 | 0 | 0
| iv) Lift lobbies | [7 empty] | FALSE | FALSE | 0 | 0
| v) Atrium | [7 empty] | FALSE | FALSE | 0 | 0
2.8 | Energy Efficiency Practices and Features
| To encourage the use of energy efficient practices and features which are innovative and/or have positive environmental impact. |  | 2 | 0 |  |  |  |  | 0
% energy savings over the total annual building energy consumption
2.9 | Renewable Energy
To encourage greater adoption and use of renewable energy.
a) | Solar Energy Feasibility Study |  | 1 | 0
| The evaluation of a building’s potential in harnessing solar energy so as to raise awareness on viable solar opportunities within the development and allow building owners to make an informed decision regarding the adoption of solar photovoltaics | [7 empty] | FALSE | 0
b) | Solar Ready Roof |  | 1.5 | 0
To encourage existing buildings to be ready for solar photovoltaic installation and facilitate their deployment should building owners decide to do so in the near future. The building development shall demonstrate solar readiness for at least 50% of the feasible roof area determined through the feasibility study. Points will be awarded for each of the following:
| i) Structural readiness: Provisions to accommodate optimised structural installation of solar panels on rooftop spaces | [7 empty] | FALSE | 0
| ii) Electrical readiness: Provisions to accommodate optimised electrical installation of solar panels on rooftop spaces | [7 empty] | FALSE | 0
| iii) Spatial readiness: Provisions to optimise the available non-shaded rooftop area for photovoltaic and/or adoption of recommendations for roof spatial optimisation outlined in the solar energy feasibility study. | [7 empty] | FALSE | 0
c) | Adoption of Renewable Energy |  | 4 | 0
To encourage on-site generation of renewable energy to reduce the building’s power consumption from the grid and carbon emissions.
| Energy Use Intensity (EUI) (kWh/m2·yr) | [7 empty] | 0 | 0
% Replacement of Total Building Electricity Consumption by Renewable Energy
0
0
MV
NV

## Control-tab (hidden)
Section 2.2
Selection 1 | Selection.no | Aircon efficiency system (for cooling load <500) | Aircon efficiency system (for cooling load ≥ 500) | System 1 cooling load | User selection | Aircon eff. System (cooling load <500) | Aircon eff. System (cooling load ≥ 500)
Water-cooled Chilled-water Plant | 2 | 0.8 | 0.75 | 500 | 1 | 0 | 0
Variable Refrigerant Flow (VRF) System | 3 | 1.1 | 1
Air-cooled Chilled-water Plant / Unitary Air-conditioners | 4 | 1.1 | 1 |  | 1. Points scored | #DIV/0!
District Cooling System | 5 |  |  |  | 2. Final points awarded | 0
(Nothing is selected) | 1
Selection 2 | Selection.no | Aircon efficiency system (for cooling load <500) | Aircon efficiency system (for cooling load ≥ 500) | System 1 cooling load | User selection | Aircon eff. System (cooling load <500) | Aircon eff. System (cooling load ≥ 500)
Water-cooled Chilled-water Plant | 2 | 0.8 | 0.75 | 500 | 1 | 0 | 0
Variable Refrigerant Flow (VRF) System | 3 | 1.1 | 1
Air-cooled Chilled-water Plant / Unitary Air-conditioners | 4 | 1.1 | 1 |  | 1. Points scored | #DIV/0!
(Nothing is selected) | 1 |  |  |  | 2. Final points awarded | 0
TRUE
Note on A3: Boon Wee ANG (BCA): Points awarded = 0.6 x (% improvement from baseline) (Up to 12 points)
Note on A4: Boon Wee ANG (BCA): Points awarded = 0.3 x (% improvement from baseline) (Up to 12 points will be awarded if permanent M&V is provided for VRF air-conditioning system. Otherwise, it is capped at 8 points.)
Note on A5: Boon Wee ANG (BCA): Points awarded = 0.3 x (% improvement from baseline) Capped at 8 points
Note on A6: Boon Wee ANG (BCA): default 12 points, multiply by percentage scored based.
Note on A11: Boon Wee ANG (BCA): Points awarded = 0.6 x (% improvement from baseline) (Up to 12 points)
Note on A12: Boon Wee ANG (BCA): Points awarded = 0.3 x (% improvement from baseline) (Up to 12 points will be awarded if permanent M&V is provided for VRF air-conditioning system. Otherwise, it is capped at 8 points.)
Note on A13: Boon Wee ANG (BCA): Points awarded = 0.3 x (% improvement from baseline) Capped at 8 points

## Section 3
SECTION 3 - RESOURCE STEWARDSHIP |  | POINTS SCORED | 0
PRE-REQUISITES |  | COMPLY
4 | WATER CONSUMPTION MONITORING |  |  |  |  | FALSE | 0
9 | RECYCLING FACILITIES |  |  |  |  | FALSE | 0
3.1 | Water Efficient Fittings | DATA INPUT | AVAILABLE POINTS | POINTS SCORED | REMARKS
| a) Points scored based on the number and water efficiency rating of the fitting type used |  | 7 | 0
| Point scored | [5 empty] | 0
| b) Attained PUB Water Efficient Building (WEB) Certificate |  |  |  |  | FALSE | 0
3.2 | Landscape Irrigation System
| To encourage use of the following for at least 50% of the landscape areas: |  | 1 | 0
| a) Water efficient irrigation systems with features such as automatic sub-soil drip irrigation and moisture or rain sensor control |  |  |  |  | FALSE | 0
| b) Drought tolerant plants |  |  |  |  | FALSE | 0
3.3 | Reduction in Water Consumption of Cooling Towers
| To encourage adoption of the following measures to reduce the consumption of potable water for the cooling towers |  | 2.5 | 0
| a) Use of a cooling tower water treatment system which can achieve 7 or better cycles of concentration with acceptable water quality |  |  |  |  | FALSE | 0
| b) Use of NEWater or alternate approved sources of water such as on-site recycled water, rainwater, Air Handling Unit (AHU) condensate, etc |  |  |  |  | FALSE | 0
| c) Use of a heat recovery system or equivalent device that helps to reduce heat rejection required through the cooling towers |  |  |  |  | FALSE | 0
Amount of water savings (m3)
3.4 | Water Monitoring and Leak Detection
| To encourage the following provisions to monitor the water consumption of the building |  | 1 | 0
| a) Private meters for all major water uses in the building |  |  |  |  | FALSE | 0
| b) Smart remote metering system with alert features for leak detection and monitoring purposes |  |  |  |  | FALSE | 0
3.5 | Water Usage Portal and Dashboard
| To encourage the adoption of water usage portal(s), dashboard(s) or other equivalent forms with the following provisions: |  | 1 | 0
| a) Display metered data, trending of water consumption and relevant parameters which facilitate better management of water consumption during building operation |  |  |  |  | FALSE | 0
| b) Allow individual tenants to monitor their own water usages and consumption |  |  |  |  | FALSE | 0
3.6 | Use of Alternative Water Sources
| To encourage use of alternative water sources for applicable non-potable uses, such as irrigation, washing, water features, toilet flushing, etc. (excluding cooling tower make up water) to reduce use of potable water. |  | 2 | 0
% reduction of potable water
3.7 | Green Products and Materials
a) | Green Products
| To encourage use of building services and mechanical and electrical (M&E) products certified by an approved local certification body. Structural components are excluded. Please indicate the green material and its respective rating and impact in the remark column. No points will be scored if information is not provided. |  | 2 | 0 |  | 0 |  | 0
| Total points scored | [6 empty] | 0.25
b) | Green Materials |  | 5 | 0 |  |  |  | 0.5
| To encourage the use of non-structural building component products certified by an approved local certification body. Structural and M&E components are excluded. Points will be awarded based on the weightage and the extent of coverage and impact (i.e. weightage x extent of coverage and impact). Please indicate the green material and its respective rating and impact in the remark column. No points will be scored if information is not provided. |  |  |  |  | 0 |  | 0.75
| Total points scored | 3 | [5 empty] | 1
3.8 | Recycling Facilities | [6 empty] | 1.25
| To encourage the provision of facilities or systems to carry out the following: |  | 3.5 | 0 |  |  |  | 1.5
| a) Collection and storage of common recyclables such as paper, glass, metal and plastic in commingled or sorted form. |  |  |  |  | FALSE | 0 | 1.75
| b) Recycling of specialised waste stream such as electronic waste, light bulbs, fluorescent tubes, and food waste. | [6 empty] | 2
| i) electronic waste |  |  |  |  | FALSE | 0 | 0
| ii) light bulbs / fluorescent tubes |  |  |  |  | FALSE | 0
| iv) food waste |  |  |  |  | FALSE | 0
| v) other specialised waste stream |  |  |  |  | FALSE | 0
| c) Consolidation of horticultural waste for recycling |  |  |  |  | FALSE | 0
3.9 | Storage Area for Recyclable Wastes
| To encourage the provision of proper dedicated storage area at a central location for recyclable wastes. |  | 1 | 0 |  | FALSE | 0
3.1 | Promotion of Waste Reduction
| To promote and encourage waste reduction and recycling among tenants, building occupants and visitors in a building |  | 2 | 0 |  |  | 0
Number of avenue of promotion
3.11 | Waste Monitoring
| To encourage the following waste collection practices in the building for continuous improvement on waste reduction |  | 2 | 0
| a) Quantifying and monitoring of the waste disposed |  |  |  |  | FALSE | 0
| b) Quantifying and monitoring of the waste recycled |  |  |  |  | FALSE | 0

## Section 4
SECTION 4 - SMART AND HEALTHY BUILDING |  | POINTS SCORED | 0
PRE-REQUISITES |  | COMPLY
6 | INDOOR TEMPERATURE |  |  |  |  | FALSE | 0
7 | INDOOR AIR QUALITY (IAQ) SURVEILLANCE AUDIT |  |  |  |  | FALSE | 0
10 | POST OCCUPANCY EVALUATION (POE) |  |  |  |  | FALSE | 0
4.1 | Occupant Comfort | DATA INPUT | AVAILABLE POINTS | POINTS SCORED | REMARKS
To encourage the following which contribute towards ensuring occupant comfort
a) | Thermal Comfort |  | 1 | 0 |  | FALSE | 0
Maintain the indoor dry-bulb temperature within 23°C to 25 °C and the relative humidity <70% for consistent indoor conditions and comfort air-conditioning.
b) | Temperature Control |  | 0.5 | 0 |  | FALSE | 0
Occupants are able to control the indoor temperature by zones according to their preference. The thermostat set point should not go below 23 ºC.
c) | Post Occupancy Evaluation (POE) |  | 2 | 0 |  | FALSE | 0
A POE survey is conducted and corrective actions are taken accordingly to promote occupant satisfaction. The POE sample size should be at least 10% of the occupant population in the building, or at least 100 for more than 1,000 occupants or 10 for less than 100 occupants in the building.
d) | Indoor Air Quality (IAQ) Management |  | 2 | 0 |  | FALSE | 0
Adoption of IAQ management practices stated in Workplace Safety and Health Guidelines – Management of Indoor Air Quality in Air-Conditioned Workplaces.
4.2 | Outdoor Air Control
To encourage the use of the following to ensure sufficient and effective ventilation to a building’s air-conditioned spaces and prevent contaminant build-up:
a) | Dedicated Outdoor Air System |  | 1 | 0 |  | FALSE | 0
Provision of a dedicated outdoor air system, such as precool units, to encourage effective treatment of the outdoor air for cooling and dehumidification.
b) | Demand Control Ventilation |  | 0.5 | 0 |  | FALSE | 0
Use of demand control ventilation strategies, such as provision of carbon dioxide (CO2) sensors or equivalent devices, to regulate the quantity of fresh air supplied to the building’s air-conditioned spaces.
4.3 | Enhanced Filtration Media
| To encourage the following for effective removal of harmful pollutants from the building’s ventilation system: |  | 2.5 | 0
| a) Provision of at least Minimum Efficiency Rating Value (MERV) 6 or equivalent filters for outdoor air filtration all the time, and at least MERV 14 or equivalent filters when the outdoor pollution level is in the unhealthy range in accordance with Ministry of Health’s guidelines. |  |  |  |  | FALSE | 0 | 0
OR
| b) Permanent provision of MERV 14 or equivalent filters to all pre-cool units (e.g. pre-cooled AHUs (PAHUs)) |  |  |  |  | FALSE | 0 | 0
| c) Permanent provision of MERV 14 or equivalent filters to all pre-cooled units and >90% coverage of AHUs (by nos.) |  |  |  |  | FALSE | 0
4.4 | Indoor Contaminants
To encourage the adoption of indoor contaminant pollution control measures and air treatment strategies that can safeguard the health of building occupants.
a) | Ultraviolet Germicidal Irradiation (UVGI) System or Equivalent Airborne Disinfection Technologies |  | 1 | 0
| Provision of an UVGI system or equivalent in AHUs to help eliminate airborne infectious micro-organisms. The UV wavelength should be of 254nm and a safety interlock for maintenance access should be provided | [5 empty] | 0
% Extent of coverage (by nos.) of a building's AHU
b) | IAQ Display
| Provision of display panels at each floor or tenancy indicating the following information to raise awareness among the tenants, building occupants and visitors on the building’s indoor air conditions: |  | 1.5 | 0
| i) Temperature |  |  |  |  | FALSE | 0
| ii) Relative humidity |  |  |  |  | FALSE | 0
| iii) CO2 concentration |  |  |  |  | FALSE | 0
4.5 | Lighting Quality
To encourage the following which contribute towards ensuring well-lit and comfortable spaces and minimising physiological discomfort for the building occupants and users:
a) | Lighting Level
| The measured indoor lighting levels should comply with the recommended illuminance (average lux level) stated in SS 531 : 2006 Code of Practice for Lighting of Work Places Part 1 – Indoor Lighting or CP 38 : 1999 Code of Practice for Artificial Lighting in Buildings |  | 1 | 0 |  | FALSE | 0
b) | Task Lights
| Provision of task lights for the building occupants and users at workstations to achieve task-appropriate illumination and flexibility for user adjustment and control |  | 1 | 0 |  | FALSE | 0
c) | Flicker-free Light Fittings
| Provision of fluorescent luminaires and LED lightings that avoid flicker and stroboscopic effects: • High frequency ballasts (frequency >20kHz) for fluorescent luminaries • LED lighting with <30% flicker |  | 1 | 0 |  | FALSE | 0
d) | Colour Rendering Index (CRI)
| Lighting should meet the minimum colour rendering index (Ra or CRI) stated in Clause 5 of SS 531: 2006 Code of Practice for Lighting of Work Places |  | 1 | 0 |  | FALSE | 0
4.6 | Acoustics
| To ensure a basic level of acoustic comfort for occupant health and well-being by minimising noise and vibration from mechanical and electrical equipment. The measured indoor sound levels should comply with the recommended ambient sound levels in SS 553 : 2009 Code of Practice for Air-Conditioning and Mechanical Ventilation in Buildings or CP 13 : 1999 Code of Practice for Air-Conditioning and Mechanical Ventilation in Buildings. |  | 1 | 0 |  | FALSE | 0
4.7 | Biophilic Features
| To encourage the provision of biophilic features in the building that improves the building occupant and users’ physical and mental well-being through the following: |  | 2 | 0
| a) Direct experience of nature (e.g. access to plants, air (sky garden), water(aquarium), etc.) |  |  |  |  | FALSE | 0
| b) Indirect experience of nature (e.g. images of nature, natural materials, texture, geometry, etc.) |  |  |  |  | FALSE | 0
4.8 | Energy Monitoring
a) | Electrical Sub-metering
| To encourage the provision of electrical sub-meter to monitor and trend log major energy use systems in the building: |  | 6 | 0
| i) Air distribution equipment, such as AHUs and/or FCUs, to be displayed in kWh and kW/RT |  |  |  |  | FALSE | 0 | 0
| ii) Lighting for common areas |  |  |  |  | FALSE | 0
| iii) Lighting for non-common areas |  |  |  |  | FALSE | 0
| iv) Lift system |  |  |  |  | FALSE | 0
| v) Escalator system |  |  |  |  | FALSE | 0
| vi) Carpark mechanical ventilation system |  |  |  |  | FALSE | 0
| vii) Any other major energy sub-systems |  |  |  |  | FALSE | 0
b) | Energy Portal and Dashboard |  | 3 | 0
To encourage the provision of an energy portal and/or dashboard, which presents the building’s energy use data in a relevant manner, to the following groups
| i) Internal building and facility management team, in the form of a digital display or web-based and mobile applications |  |  |  |  | FALSE | 0 | 0
| ii) Building occupants and visitors, in the form of digital displays in common areas |  |  |  |  | FALSE | 0
| iii) Tenants, showing the total energy consumption of the building and the individual tenant consumption |  |  |  |  | FALSE | 0
c) | Building Management System (BMS) and Controllers with Open Protocol |  | 1 | 0
| To encourage the use of BACnet, Modbus or any other non-proprietary protocol as the network of the building management system (BMS). The BMS shall be able to provide scheduled export of a set of any chosen data points with time stamp to commonly used file formats such as .csv or .xls. |  |  |  |  | FALSE | 0
d) | Connection to BCA Smart Chiller Portal |  | 1 | 0
| To connect/provide the building chiller plant performance data to the BCA Smart Chiller Portal. |  |  |  |  | FALSE | 0
4.9 | Demand Control
| To encourage the use of occupancy-based controls to monitor and regulate the temperature, airflow, or lighting brightness of the following spaces in the building to optimise the building’s energy consumption for air-conditioning, mechanical ventilation (ACMV) and lighting |  | 5 | 0
Common Areas such as:
| i) Toilets |  |  |  |  | FALSE | 0 | 0 |  | a) Use adaptive control algorithms to improve equipment efficiency | a) Whole system optimisation using a network of HVAC equipment
| ii) Staircases |  |  |  |  | FALSE | 0 |  |  | b) Identify systems that deviate from statistically expected performance | b) Integration of sub-systems to optimise resource use or improve user experience
| iii) Corridors |  |  |  |  | FALSE | 0 |  |  | c) Detect equipment that run beyond operating hours or routine settings | c) Use of Building Information Modelling (BIM) or similar applications that provide location-based visualisation of multiple sensors
| iv) Lift lobbies |  |  |  |  | FALSE | 0 |  |  | d) Monitor equipment condition for preventive maintenance | d) Participate in a Demand Response programme
| v) Atriums |  |  |  |  | FALSE | 0 |  |  | e) Detect deviation to find improperly operating sensors or actuators
Tenanted/ Normally occupied areas
| % coverage of occupied area, such as offices, retail shops or hotel guest rooms | [6 empty] | 0 | 0
4.1 | Integration and Analytics
To encourage the integrative use of data to optimise workflow or sustain high performance and energy efficiency in a building.
a) | Basic Integration and Analytics |  | 2 | 0
[7 empty] | 0 | 0 | 2
Description of basic integration and analytics
[7 empty] | 0 |  | 1
Description of basic integration and analytics
[7 empty] | 0 |  | 1
| Description of basic integration and analytics |  |  |  |  | FALSE | 0
4
Description of basic integration and analytics
b) | Advanced Integration and Analytics |  | 3 | 0
[7 empty] | 0 | 0 | 2
Description of advanced integration and analytics
[7 empty] | 0 |  | 1
Description of advanced integration and analytics
[7 empty] | 0 |  | 1
Description of advanced integration and analytics

## Section 5
SECTION 5 - ADVANCED GREEN EFFORT |  | POINTS SCORED | 2
5.1 | Accredited Green Facility Management Companies | DATA INPUT | AVAILABLE POINTS | POINTS SCORED | REMARKS
| To encourage the engagement of Green Facility Management (FM) companies, accredited by the Singapore Green Building Council (SGBC) or equivalent, in the sustainable operation and maintenance of the building |  | 1 | 0 |  | FALSE | 0
5.2 | ETTV < 40W/m2 |  | 1 | 0
| To encourage good thermal performance of a building envelope to minimise heat gain into the building. |  |  |  |  | 0
| Envelope Thermal Transfer Value (ETTV) (W/m2) | 0
5.3 | Demonstration of Better Air Distribution System Efficiency |  | 2 | 0
| To encourage better air distribution system efficiency of less than 0.2 kW/RT (Baseline = 0.28 kW/RT). The efficiency should be demonstrated via an energy audit. | [5 empty] | 0
| % Improvement from baseline | 0
5.4 | Renewable Energy
| a) Further Electricity Replacement By On-site Renewable Energy (Section 2.9c) |  | 6 | 0 |  | 0 | 0
| % Electricity Replacement | 0
| b) Purchase of Renewable Energy From Licenced Electricity Retailers Minimum 5% of total building energy to be purchased from renewable energy sources and a minimum contract period of 3 years) |  | 1 | 0 |  | FALSE | 0
| c) Roof leasing for Photovoltaic installation |  | 1.5 | 0 |  | FALSE | 0
5.5 | Thermal Comfort with Elevated Air Speed
| Use of innovative solutions, such as high temperature cooling with increased air speed, to achieve thermal comfort conditions while reducing energy consumption |  | 2 | 0
| Demonstrate compliance with thermal comfort criteria (-0.5 < PMV < 0.5 and/or PPD < 10%) through ASHRAE 55, ISO 7730 or EN15251 methodologies, and energy savings through actual metering |  |  |  |  | FALSE | 0
Indoor temperature maintained at 26oC and above
5.6 | IAQ Surveillance Audit
| IAQ surveillance audit is conducted once every 3 years by an accredited laboratory under Singapore Accreditation Council with respect to the recommended IAQ parameters and acceptable limits stated in Table 1 of SS554: 2016 based on the reference methods. |  | 2 | 0 |  | FALSE | 0
5.7 | Outdoor Airflow Monitoring System
| To measure and monitor the outdoor airflow volume in the following by permanent devices to ensure provision of sufficient ventilation for various spaces, in accordance with desired ventilation rates. |  | 2 | 0
| a) All precool units (e.g. PAHUs) |  |  |  |  | FALSE | 0
| b) > 90% coverage (by nos.) of a building’s all AHUs and/or FCUs |  |  |  |  | FALSE | 0
5.8 | SGBC or equivalent Certified Air Filters
| Use of SGBC or equivalent certified air filters at all AHUs including PAHUs. |  | 1 | 0
0
| SGBC Rating of air filter | [7 empty] | Good | 0
5.9 | Indoor Air Quality Trending and Monitoring | [7 empty] | Very Good
| To provide permanent trend logging and monitoring of the following parameters, with at least 1 measuring point per floor and linked to a centralised system. |  | 4 | 0 |  |  |  |  | Excellent
| a) Temperature and relative humidity |  |  |  |  | FALSE | 0 |  | Leader
b) Common Indoor Air Pollutants
| i) Formaldehyde |  |  |  |  | FALSE | 0
| ii) Total Volatile Organic Compounds (TVOC) |  |  |  |  | FALSE | 0
| iii) Particulate Matters |  |  |  |  | FALSE | 0
5.1 | Local Exhaust and Air Purging System
| a) Local isolation and exhaust systems to remove the pollutants at source, e.g. photocopier room with exhaust system |  | 1 | 0 |  | FALSE | 0
| b) Air purging system to replace contaminated indoor air with outdoor fresh air |  |  |  |  | FALSE | 0
5.11 | Permanent M&V for Variable Refrigerant Flow (VRF) system
| a) Power meters installed for all condensing units of the VRF system |  | 3 | 0 |  | FALSE | 0
| b) Provision of permanent measuring instruments for monitoring of the energy efficiency performance of the VRF condensing units and air distribution sub-system. The installed instrumentation shall have the capability to calculate resultant system efficiency (i.e. KW/RT or Coefficient of Performance (COP)) within ±10% uncertainty. Each measurement system shall include the sensor, any signal conditioning, the data acquisition system and wiring connecting them. All data are to be logged at 5-minute sampling time interval, recorded to at least 1 decimal point, and available for extraction for verification purposes. |  |  |  |  | FALSE | 0
5.12 | Complementary Certifications
| To encourage tenants in a building to take up certification of their tenanted areas or premises under the BCA Green Mark occupant-centric schemes |  | 2 | 0
| a) At least 1 tenant certified under a Green Mark occupant-centric scheme |  |  |  |  | FALSE | 0
| b) The building achieves the BCA Green Mark Pearl Award |  |  |  |  | FALSE | 0
| c) The building achieves the BCA Green Mark Pearl Prestige Award |  |  |  |  | FALSE | 0
5.13 | Display of BCA Green Mark Plaque and Decal
| To encourage display of the BCA Green Mark Plaque or Decal at a prominent location in the building, such as the foyer or main lobby. |  | 1 | 0 |  | FALSE | 0
5.14 | Display of BCA Green Mark Plaque and Decal
| a) To encourage the best practice for hot water system operation, points will be awarded to buildings’ Hot Water System Ratio (HWSR) which is better than baseline. |  | 3 | 0
| Hot Water System Ratio |  |  |  |  | 0 | 0
| b) Provision of permanent measuring instruments for monitoring of Hot Water System Ratio |  |  |  |  | FALSE | 0
| c) Measure Heat loss from Hot Water system, can be from third party energy audit or permanent M&V |  |  |  |  | FALSE | 0 |  | Low impact
5.15 | Persistent Bio-Cumulative and Toxic (PBT) Free Lighting | [7 empty] | Medium Impact
| Provision of Persistent Bio-cumulative and Toxic (PBT) free lighting |  | 0.5 | 0 |  | FALSE | 0 |  | High Impact
5.16 | Adoption of Smart Facilities Management (FM)
To encourage the adoption of Smart FM in area such as M&E services, security, environmental services etc to improve workflow processes, increase productivity and enhance service delivery for sustainable operation and maintenance of the building.
| a) Conduct a feasibility study using the 5-step SMART process template including cost benefit analysis |  | 0.5 | 0 |  | FALSE | 0 |  | Low impact
| b) Implementation of smart technology solutions such as -Usage of robotics for feedback and optimisation of processes -Usage of video monitoring coupled with facial recognition for incident detection in security function -Workflow automation to streamline FM services with feedback loop -Use of digital twin to monitor assets and enable predictive maintenance |  | 2.5 | 0 |  |  |  |  | High Impact
| i) Smart Technology Solution |  |  |  |  | 1 | 0 | 0
Description of smart technology solution
| ii) Smart Technology Solution |  |  |  |  | 1 | 0 | 0
Description of smart technology solution
| iii) Smart Technology Solution |  |  |  |  | 1 | 0 | 0
Description of smart technology solution
| iii) Smart Technology Solution |  |  |  |  | 1 | 0 | 0
Description of smart technology solution
5.17 | Other Advanced Green Efforts
| Buildings which demonstrate substantial and exemplary performance to a specific sustainability indicator or outcome addressed within Green Mark beyond what is specified in the criteria, assessed on a case-by-case basis |  |  | 2 |  |  |  | 0 | 0
| i) Advanced Green Effort |  |  |  |  | 1 | 0 | 0
Description of Other Advanced Green Efforts
| ii) Advanced Green Effort |  |  |  |  | 1 | 0 | 0
Description of Other Advanced Green Efforts
| iii) Advanced Green Effort |  |  |  |  | 1 | 0 | 0
Description of Other Advanced Green Efforts
| iv) Advanced Green Effort |  |  |  |  | 1 | 0 | 0
Description of Other Advanced Green Efforts
| v) Advanced Green Effort |  |  |  |  | 1 | 0 | 0
Description of Other Advanced Green Efforts
| vi) Advanced Green Effort | dd |  |  |  | 4 | 2 | 2
Description of Other Advanced Green Efforts