## Instructions
Instructions
This Retrofit Proposal/Report template is to guide applicants in the preparation of the information related to the proposed Energy Improvement Works (EIWs) required for the GMIS-EB 2.0 Scheme/Tranche Applications. This document is one of the document required to complete the Scheme/Tranche Applications; failure to submit a complete application may result in the application being rejected.
Fields to complete
1. Scheme Application stage: a. All pre-retrofit fields in the 'Project Details' tab b. All pre-retrofit fields for all proposed EIWs in the 'System Level' tabs. Proposed calculation methods for common systems like Chiller Plant, AHU system, Mechanical Ventilation system and Lighting have been prepared in this excel. For other proposed EIWs, provide similar information/calculations under the 'Other Measures' tab and add on more tabs for more measure, if necessary. c. Cells B to D in the 'Proposed Qualifying Costs' tab d. Ensure the details ported over from the 'System Level' tabs to the 'Proposal Summary' is correct and update the details for the EIWs from the 'Other Measures' tab(s), where necessary. 2. First Tranche Application stage: a. Cells D to H in the 'Disbursement Application' tab 3. Second Tranche Application stage: a. All post-retrofit fields in the 'Project Details' tab b. All post-retrofit fields for all proposed EIWs in the 'System Level' tabs. c. Cells D to H in the 'Disbursement Application' tab
Quick Info on Scheme Details
1. Qualifying Criteria:
Green Mark Rating | Funding Factor ($ per tCO2e) | Funding Cap ($)
Green Mark Platinum | 25 | 600000 | or up to 50% of qualifying cost, whichever is lower
Green Mark Super Low Energy (SLE) | 35 | 900000 | or up to 50% of qualifying cost, whichever is lower
Green Mark Zero Energy (ZE) | 45 | 1200000 | or up to 50% of qualifying cost, whichever is lower
2. Other Scheme Requirement:
a. All proposed Energy Improvement Works (EIWs) must be installed with a permanent M&V instrumentation.
Quick Links
1. GMIS-EB 2.0 Webpage: |  | https://www1.bca.gov.sg/buildsg/sustainability/green-mark-incentive-schemes/green-mark-incentive-scheme-for-existing-buildings-2.0
2. GM 2021 Assessment Criteria Webpage: |  | https://www1.bca.gov.sg/buildsg/sustainability/green-mark-certification-scheme/green-mark-2021
3. Energy Efficiency Calculator for Green Mark Assessment/Verification: |  | https://sleb.sg/AICalculator
4. Technologies supporting Super Low Energy Building: |  | https://www.sleb.sg/Technologies

## Declaration
Instructions
This Retrofit Proposal/Report is to be endorsed by a third-party Qualified Professional. All fields and declaration below are to be completed.
Details of third-party Qualified Professional endorsing the Retrofit Proposal (Scheme Application Stage)
Name
Certification
Company
Email
Declaration by the third-party Qualified Professional (to indicate 'Yes" under column B)
a) I hereby certify that the figures and statements in this Retrofit Proposal and the accompanying supporting technical documents i) are true and correct to the best of my knowledge and that I have not withheld/distorted any facts and ii) have been verified to their original source.
b) I understand that if I had endorsed this Retrofit Proposal to obtain any benefits under the Scheme by false, misleading statements, BCA may, at its discretion, withdraw its LOA and recover from the Applicant such sums and in such a manner as set out in the Scheme T&Cs.
Signature:
Details of third-party Qualified Professional endorsing the Retrofit Report (Second Tranche Application Stage)
Name
Certification
Company
Email
Declaration by the third-party Qualified Professional (to indicate 'Yes" under column B)
a) I hereby certify that the figures and statements in this Retrofit Report and the accompanying supporting technical documents i) are true and correct to the best of my knowledge and that I have not withheld/distorted any facts and ii) have been verified to their original source.
b) I understand that if I had endorsed this Retrofit Report to obtain any benefits under the Scheme by false, misleading statements, BCA may, at its discretion, withdraw its LOA and recover from the Applicant such sums and in such a manner as set out in the Scheme T&Cs.
Signature:
Note: Please print out this declaration tab and have the third-party Qualified Professional ink-sign. Please also upload this scanned endorsed page as part of Scheme Application/ Second Tranche Application documents.

## Project Details
Instructions
| To complete fields under 'Pre-Retrofit' at Scheme Application Stage 1. All fields must be completed 2. EUI is auto-computed | To complete fields under 'Post-Retrofit' at Second Tranche Application Stage 1. All fields must be completed 2. Indicate no change if info provided at pre-retrofit stage is still relevant
| Pre-Retrofit: | Post-Retrofit:
Building Name: | (for QP's input) | e.g. no change
Building Owner: | (for QP's input) | e.g. no change
GM rating: | Platinum | Platinum
Building operating hours: (breakdown by use types) | e.g. Office: Total 61 hrs/wk - Weekdays (7am-6pm=11 hrs) = 55 hrs/wk - Saturdays (7am-1pm= 6 hrs) = 6 hrs/wk Retail: Total 101.5 hrs/wk - Full week (7.30am-10pm=14.5 hrs) = 101.5hrs/wk | no change
Building occupancy rate: | e.g. 85% | e.g. 85%
GFA (m2) |  | e.g. no change
Total Consumption Per Year (kwh/yr):
EUI (kwh/yr/m2): | 0 | 0

## Chiller Plant
CHILLER PLANT
Instructions
|  | To complete fields under "Pre-Retrofit" at Scheme Application Stage 1. All fields must be completed if Chiller Plant works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Chiller Plant Works', providing details on: a. the current state of the equipment b. retrofitting works involved, including installation of M&V instrumentation c. the M&V conducted to determine the baseline energy consumption of the current equipment (to provide 2 weeks logged data) d. the proposed M&V plan conducted to determine the actual energy consumption of the retrofitted equipment (should be using similar/comparable method as item c and to provide 2 weeks logged data). 3. Provide calculations to determine the measured energy consumption of the current equipment and estimated energy consumption of the equipment post-retrofit in order to determine the Estimated Energy Savings from this EIW | [7 empty] | To complete fields under "Post-Retrofit" at Second Tranche Application Stage 1. All fields must be completed if Chiller Plant works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Chiller Plant Works', providing details on (Indicate no change if info provided at pre-retrofit stage is still relevant): a. retrofitting works involved, including installation of M&V instrumentation b. the M&V conducted to determine the actual energy consumptino of the retrofitted equipment (to provide 2 weeks logged data) c. provide photographic evidence of the M&V instrumentation installed 3. To provide calculations to determine the measured energy consumption of the retrofitted equipment and in order to determine the Actual Energy Savings from this EIW
|  | Pre-Retrofit | [7 empty] | Post-Retrofit
Details of Proposed Chiller Plant Works
| Current state and works involved: | [8 empty] | Any changes to the information provided under "Details of Proposed Chiller Plant Works" pre-retrofit? (For third-party Qualified Professional's declaration)
If "No", pls declare "No". If "Yes", pls elaborate on the changes.
M&V plan to determine energy consumption pre-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals
Photographic evidence of M&V instrumentation installed
Proposed M&V plan to determine energy consumption post-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals - equations and/or simulation methodologies used to derive the consumption and performance
Calculations
| Pre-Retrofit |  |  |  | Proposed | [5 empty] | Actual
| Chiller Plant configuration | e.g. 2 x 550RT, 1 x 300RT |  |  | Chiller Plant configuration |  | e.g. 2 x 550RT, 1 x 300RT |  |  |  | Chiller Plant configuration |  | e.g. 2 x 550RT, 1 x 300RT
| Operating Cooling Load | e.g. 810 RT |  |  | Operating Cooling Load |  | e.g. 810 RT |  |  |  | Operating Cooling Load |  | e.g. 810 RT
| Operating Hours | e.g. 1x550 RT 9AM to 6PM, 1 x 300RT 6PM to 9AM |  |  | Operating Hours |  | e.g. 1x550 RT 9AM to 6PM, 1 x 300RT 6PM to 9AM |  |  |  | Operating Hours |  | e.g. 1x550 RT 9AM to 6PM, 1 x 300RT 6PM to 9AM
| Measurement performed by | e.g. Esco ESD Pte Ltd |  |  | Measurement performed by |  | e.g. Esco ESD Pte Ltd |  |  |  | Measurement performed by |  | e.g. Esco ESD Pte Ltd
| Checked & submitted by | e.g. EA Peter Tan (EA no. 34) |  |  | Checked & submitted by |  | e.g. EA Peter Tan (EA no. 34) |  |  |  | Checked & submitted by |  | e.g. EA Peter Tan (EA no. 34)
| Chiller Plant Equipment | Pre-Retrofit (Measured Data) |  |  | Proposed |  |  | Saving kWh | kW/RT % Improvement |  | Actual (Measured Data) |  |  | Saving kWh | kW/RT % Improvement
|  | Cooling load (RTh) | kWh | kW/RT | Cooling load (RTh) | kWh | kW/RT |  |  |  | Cooling load (RTh) | kWh | kW/RT
| Chillers | 2639132.4473 | 2320047.2986 | 0.87909 | 2642954.3743 | 1358010.6356 | 0.51382 | 962036.663 | 41.55% |  | 2564394 | 1286136.0926 | 0.50154 | 1033911.2059 | 42.95%
| Chilled Water Pumps |  | 600225.45 | 0.22743 |  | 88140.9625 | 0.033349 | 512084.4875 | 85.34% |  |  | 101728.168 | 0.039669 | 498497.282 | 82.56%
| Condenser Water Pumps |  | 329513.7316 | 0.12486 |  | 83480.1719 | 0.031586 | 246033.5598 | 74.7% |  |  | 83480.1719 | 0.032554 | 246033.5598 | 73.93%
| Cooling Towers |  | 185268.4661 | 0.070201 |  | 60346.6189 | 0.022833 | 124921.8472 | 67.47% |  |  | 60346.6189 | 0.023533 | 124921.8472 | 66.48%
| Total Chiller Plant |  | 3435054.9463 | 1.3016 |  | 1589978.3889 | 0.60159 | 1845076.5575 | 53.78% |  |  | 1531691.0514 | 0.59729 | 1903363.895 | 54.11%
[5 empty] | Estimated Energy Savings from Chiller Plant Works |  |  | 1845076.5575 | kWh/yr |  | Actual Energy Savings from Chiller Plant Works |  |  | 1903363.895 | kWh/yr

## AHU
AIR-DISTRIBUTION SYSTEM
Instructions
|  | To complete fields under "Pre-Retrofit" at Scheme Application Stage 1. All fields must be completed if AHU works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed AHU Works', providing details on: a. the current state of the equipment b. retrofitting works involved, including installation of M&V instrumentation c. the M&V conducted to determine the baseline energy consumption of the current equipment (to provide 2 weeks logged data) d. the proposed M&V plan conducted to determine the actual energy consumption of the retrofitted equipment (should be using similar/comparable method as item c and to provide 2 weeks logged data). 3. Provide calculations to determine the measured energy consumption of the current equipment and estimated energy consumption of the equipment post-retrofit in order to determine the Estimated Energy Savings from this EIW | [10 empty] | To complete fields under "Post-Retrofit" at Second Tranche Application Stage 1. All fields must be completed if AHU works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Chiller Plant Works', providing details on (Indicate no change if info provided at pre-retrofit stage is still relevant): a. retrofitting works involved, including installation of M&V instrumentation b. the M&V conducted to determine the actual energy consumption of the retrofitted equipment (to provide 2 weeks logged data) c. provide photographic evidence of the M&V instrumentation installed 3. To provide calculations to determine the measured energy consumption of the retrofitted equipment and in order to determine the Actual Energy Savings from this EIW
| Pre-Retrofit | [11 empty] | Post-Retrofit
Details of Proposed AHU Works
| Current state and works involved: | [11 empty] | Any changes to the information provided under "Details of Proposed Chiller Plant Works" pre-retrofit? (For third-party Qualified Professional's declaration)
If "No", pls declare "No". If "Yes", pls elaborate on the changes.
M&V plan to determine energy consumption pre-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals
Photographic evidence of M&V instrumentation installed
Proposed M&V plan to determine energy consumption post-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals - equations and/or simulation methodologies used to derive the consumption and performance
Calculations
Note:
1) Existing AHUs are measured at AHU panels.
2) Using affinity law for projected power consumption where New Power2 = Old Power1 x (N2/N1)^3.
3) New AHUs to be measured from new AHU panels or from VSD for 2 weeks.
4) Current table assumes no change in building use types. If there is a change in use types (e.g. from retail to office) affecting the operating hours, pls add in an additional column to show the new operating hours.
|  |  | Pre-Retrofit |  |  |  | Proposed | [5 empty] | Actual (Post-retrofit)
|  |  | Building Operating Hours as defined under "Project Details" (hrs/yr) | EXISTING AHUs (Measured data) |  |  | NEW AHUs Specification (After replacement) |  |  | NEW AHUs Projected Operation (After replacement @ 40Hz) |  |  | NEW AHUs Actual Operation
| Area Served (according to Building Operating Hours as defined under "Project Details") e.g. Office, Retail | Equipment ID | e.g. Office: Total 61 hrs/wk - Weekdays (7am-6pm=11 hrs) = 55 hrs/wk - Saturdays (7am-1pm= 6 hrs) = 6 hrs/wk Retail: Total 101.5 hrs/wk - Full week (7.30am-10pm=14.5 hrs) = 101.5hrs/wk | VSD (Hz) | Fan Motor kW | Power consumption kWh/yr | Air Flow CMH | Fan Motor kW | Cooling Capacity RT | VSD (Hz) | Fan Motor kW @ 40Hz | Power consumption kWh/yr | VSD (Hz) | Fan Motor kW (Measured) | Power consumption kWh/yr
| Office | AHU 1 | 3900 | No VSD | 5.5 | 21450 | 11550 | 4 | 20.77 | 40 | 2.048 | 7987.2 | 40 | 1.934 | 7542.6
| Office | AHU 2 | 3900 |  | 11 | 42900 | 19800 | 7.5 | 34.62 | 40 | 3.84 | 14976 | 40 | 3.945 | 15385.5
| Office | AHU 3 | 3900 |  | 11 | 42900 | 29700 | 11 | 57.12 | 40 | 5.632 | 21964.8 | 40 | 5.698 | 22222.2
| Office | AHU 4 | 3900 |  | 11 | 42900 | 27467 | 11 | 44.51 | 40 | 5.632 | 21964.8 | 40 | 5.789 | 22577.1
| Office | AHU 5 | 3900 |  | 15 | 58500 | 32000 | 15 | 60.05 | 40 | 7.68 | 29952 | 40 | 7.304 | 28485.6
| Office | AHU 6 | 3900 |  | 22 | 85800 | 56856 | 18.5 | 84.16 | 40 | 9.472 | 36940.8 | 40 | 9.634 | 37572.6
| Retail | AHU 7 | 3900 |  | 30 | 117000 | 60000 | 18.5 | 97.12 | 40 | 9.472 | 36940.8 | 40 | 9.652 | 37642.8
| Retail | AHU 8 | 3900 |  | 15 | 58500 | 35187 | 15 | 62.66 | 40 | 7.68 | 29952 | 40 | 7.723 | 30119.7
| Retail | AHU 9 | 3900 |  | 22 | 85800 | 65000 | 18.5 | 102.13 | 40 | 9.472 | 36940.8 | 40 | 9.105 | 35509.5
| Retail | AHU 10 | 3900 |  | 15 | 58500 | 35346 | 15 | 62.9 | 40 | 7.68 | 29952 | 40 | 7.305 | 28489.5
|  |  |  | Total | 157.5 | 614250 |  |  |  | Total | 68.608 | 267571.2 | Total | 68.089 | 265547.1
| Measured Energy Consumption before retrofitting works |  |  |  |  | 614250 | kWh/yr | [6 empty] | Measured Energy Consumption after retrofitting works |  | 265547.1 | kWh/yr
| Estimated Energy Consumption after retrofitting works |  |  |  |  | 267571.2 | kWh/yr | [6 empty] | Actual Energy Savings from AHU works |  | 348702.9 | kWh/yr
| Estimated Energy Savings from AHU works |  |  |  |  | 346678.8 | kWh/yr

## Mechanical Ventilation
MECHANICAL VENTILATION [MV] (CARPARK ETC)
Instructions
|  | To complete fields under "Pre-Retrofit" at Scheme Application Stage 1. All fields must be completed if Mechanical Ventilation works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Mechanical Ventilation Works', providing details on: a. the current state of the equipment b. retrofitting works involved, including installation of M&V instrumentation c. the M&V conducted to determine the baseline energy consumption of the current equipment (to provide 2 weeks logged data) d. the proposed M&V plan conducted to determine the actual energy consumption of the retrofitted equipment (should be using similar/comparable method as item c and to provide 2 weeks logged data). 3. Provide calculations to determine the measured energy consumption of the current equipment and estimated energy consumption of the equipment post-retrofit in order to determine the Estimated Energy Savings from this EIW | [7 empty] | To complete fields under "Post-Retrofit" at Second Tranche Application Stage 1. All fields must be completed if Mechanical Ventilation works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Mechnical Ventilation Works', providing details on (Indicate no change if info provided at pre-retrofit stage is still relevant): a. retrofitting works involved, including installation of M&V instrumentation b. the M&V conducted to determine the actual energy consumption of the retrofitted equipment (to provide 2 weeks logged data) c. provide photographic evidence of the M&V instrumentation installed 3. To provide calculations to determine the measured energy consumption of the retrofitted equipment and in order to determine the Actual Energy Savings from this EIW
|  | Pre-Retrofit | [7 empty] | Post-Retrofit
Details of Proposed MV Works
| Current state and works involved: | [8 empty] | Any changes to the information provided under "Details of Proposed Chiller Plant Works" pre-retrofit? (For third-party Qualified Professional's declaration)
If "No", pls declare "No". If "Yes", pls elaborate on the changes.
M&V plan to determine energy consumption pre-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals
Photographic evidence of M&V instrumentation installed
Proposed M&V plan to determine energy consumption post-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals - equations and/or simulation methodologies used to derive the consumption and performance
Calculations
Note:
1) Fans' operating power to be trended & measured from fan panels for 2 weeks.
2) Assumptions for operations of Fans with VSD and CO sensor as follows:
a. Fans operate at full speed during the morning (1h), afternoon (2h) and evening (1h) on weekdays due to high volume traffic
b. Fans operate at full speed during the morning (1h) and afternoon (1h) on Saturdays due to high volume traffic
c. Fans operating at 25Hz during low volume traffic hours to maintain air flow in the car park space
d. Based on the affinity law, rated power shall be 0.69kW at 25Hz for a 5.5kW full rated power
| Pre-retrofit |  |  |  | Proposed | [5 empty] | Actual (Post-retrofit)
| Equipment | Weekly Operating Hours (h/wk) | Operating Power (kW) | Pre-retrofit Annual Energy Consumption (kWh/yr) | Equipment | Fans operating strategy with VSD & CO sensors | Weekly Operating Hours (h/wk) | Operating Power (kW) | Projected Annual Consumption (kWh/yr) |  | Equipment | Fans operating strategy with VSD & CO sensors | Weekly Operating Hours (h/wk) | Operating Power (kW) | Actual Annual Consumption (kWh/yr)
|  | A | B | A x B x 52 |  |  | A | B | A x B x 52 |  |  |  | A | B | A x B x 52
| EAF/B-1 | 55 | 5.5 | 15730 | EAF/B-1 | Fans at Full speed for 4 hrs daily on weekdays & 2 hrs on Saturday | 22 | 5.5 | 6292 |  | EAF/B-1 | Fans at Full speed for 4 hrs daily on weekdays & 2 hrs on Saturday | 22 | 5.5 | 6292
| SAF/B-1 | 55 | 5.5 | 15730 |  | Fans at 25Hz during low volume traffic hours | 33 | 0.6875 | 1179.75 |  |  | Fans at 25Hz during low volume traffic hours | 33 | 0.6875 | 1179.75
| Total |  |  | 31460 | SAF/B-1 | Fans at Full speed for 4 hrs daily on weekdays & 2 hrs on Saturday | 22 | 5.5 | 6292 |  | SAF/B-1 | Fans at Full speed for 4 hrs daily on weekdays & 2 hrs on Saturday | 22 | 5.5 | 6292
[6 empty] | Fans at 25Hz during low volume traffic hours | 33 | 0.6875 | 1179.75 |  |  | Fans at 25Hz during low volume traffic hours | 33 | 0.6875 | 1179.75
[5 empty] | Total |  |  |  | 14943.5 |  | Total |  |  |  | 14943.5
| Estimated Energy Savings from Mechanical Ventilation works | [5 empty] | 16516.5 | kWh/yr |  | Actual Energy Savings from Mechanical Ventilation works |  |  | 16516.5 | kWh/yr

## Lighting
LIGHTING
Instructions
|  | To complete fields under "Pre-Retrofit" at Scheme Application Stage 1. All fields must be completed if Lighting works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Lighting Works', providing details on: a. the current state of the equipment b. retrofitting works involved, including installation of M&V instrumentation c. the M&V conducted to determine the baseline energy consumption of the current equipment (to provide 2 weeks logged data) d. the proposed M&V plan conducted to determine the actual energy consumption of the retrofitted equipment (should be using similar/comparable method as item c and to provide 2 weeks logged data). 3. Provide calculations to determine the measured energy consumption of the current equipment and estimated energy consumption of the equipment post-retrofit in order to determine the Estimated Energy Savings from this EIW | [9 empty] | To complete fields under "Post-Retrofit" at Second Tranche Application Stage 1. All fields must be completed if Lighting works is one of the proposed EIWs the applicant is claiming under the scheme 2. To provide elaboration under 'Details of Proposed Lighting Works', providing details on (Indicate no change if info provided at pre-retrofit stage is still relevant): a. retrofitting works involved, including installation of M&V instrumentation b. the M&V conducted to determine the actual energy consumption of the retrofitted equipment (to provide 2 weeks logged data) c. provide photographic evidence of the M&V instrumentation installed 3. To provide calculations to determine the measured energy consumption of the retrofitted equipment and in order to determine the Actual Energy Savings from this EIW
|  | Pre-Retrofit | [9 empty] | Post-Retrofit
Details of Proposed Lighting Works
| Current state and works involved: | [10 empty] | Any changes to the information provided under "Details of Proposed Chiller Plant Works" pre-retrofit? (For third-party Qualified Professional's declaration)
If "No", pls declare "No". If "Yes", pls elaborate on the changes.
M&V plan to determine energy consumption pre-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals
Photographic evidence of M&V instrumentation installed
Proposed M&V plan to determine energy consumption post-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals - equations and/or simulation methodologies used to derive the consumption and performance
Calculations
|  | Pre-Retrofit |  |  |  |  | Proposed | [5 empty] | Actual (Post-Retrofit)
| Location | Type of Fittings | Power per fitting (W) | No. of Fittings | Operating Hours (hrs) | Total power (kWh/yr) | Type of Fittings | Power per fitting (W) | No. of Fittings | Operating Hours (hrs) | Total power (kWh/yr) | Location | Type of Fittings | Power per fitting (W) | No. of Fittings | Operating Hours (hrs) | Total power (kWh/yr)
|  |  | A | B | C | D = A x B x C x 365 / 1000 |  | E | F | G | H = E x F x G x 365 / 1000 |  |  | E | F | G | H = E x F x G x 365 / 1000
|  | e.g. 1 x 36W T8 |  |  |  | 0 | e.g. 1 x 36W T8 |  |  |  | 0 |  | e.g. 1 x 36W T8 |  |  |  | 0
[6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0
[6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0
[6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0
[6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0
[6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0
|  | Total Measured Consumption |  |  |  | 0 | Total Estimated Consumption |  |  |  | 0 |  | Total Consumption |  |  |  | 0
| Estimated Energy Savings from Lightings Works |  |  |  |  | 0 | kWh/yr |  |  |  |  | Actual Energy Savings from Lightings Works |  |  |  | 0 | kWh/yr

## Other Measures
OTHER MEASURES
Instructions
|  | To complete fields under "Pre-Retrofit" at Scheme Application Stage for other proposed EIWs that the applicant is claiming under the scheme (1 tab per additional measure) 1. All fields must be completed 2. To provide elaboration under 'Details of Proposed Works', providing details on: a. the current state of the equipment, system or space b. retrofitting works involved, including installation of M&V instrumentation c. the M&V conducted to determine the baseline energy consumption of the current equipment (to provide 2 weeks logged data) d. the proposed M&V plan conducted to determine the actual energy consumption of the retrofitted equipment (should be using similar/comparable method as item c and to provide 2 weeks logged data). 3. Provide calculations to determine the measured energy consumption of the current equipment and estimated energy consumption of the equipment post-retrofit in order to determine the Estimated Energy Savings from this EIW. 4. To list down any assumptions used in the calculations, where applicable. | To complete fields under "Post-Retrofit" at Second Tranche Application Stage for other proposed EIWs that the applicant is claiming under the scheme (1 tab per additional measure) 1. All fields must be completed 2. To provide elaboration under 'Details of Proposed Works', providing details on (Indicate no change if info provided at pre-retrofit stage is still relevant): a. retrofitting works involved, including installation of M&V instrumentation b. the M&V conducted to determine the actual energy consumption of the retrofitted equipment (to provide 2 weeks logged data) c. provide photographic evidence of the M&V instrumentation installed 3. To provide calculations to determine the measured energy consumption of the retrofitted equipment and in order to determine the Actual Energy Savings from this EIW 4. To list down any assumptions used in the calculations, where applicable.
Guidance Notes
Some guidelines on calculation for energy savings and carbon abated from other measures: e.g. Adoption of smart building energy management technologies to optimise systems, i.e. water-cooled chiller plant system, would result in a reduction of energy consumption. The contribution to energy savings and hence carbon abated, should be factored in the proposed post-project state of the system. Suitable estimates on % improvement should be utilised in the calculations for estimated energy savings. Post-project state to be verified in the measured energy consumption of the optimised system. e.g. conversion of existing AC area to Natural Ventilation or Mixed Mode Ventilation would result in a reduction of cooling load demand and energy consumption from the air-conditioning system and changes to air distribution system. The contribution to energy savings and hence carbon abated by the converted space, should be factored in the proposed post-project state of the air-conditioning and air distribution system, considering introduction of new mechanical ventilation equipment, if needed. Post-project state to be verified in the measured energy consumption of the optimised systems. For MMV, additional energy consumption from mechanical ventilation introduced should be metered and deducted from the total energy savings from air-conditioning system.
|  | Pre-Retrofit | Post-Retrofit
Details of Proposed Works
| Current state and works involved: |  | Any changes to the information provided under "Details of Proposed Chiller Plant Works" pre-retrofit? (For third-party Qualified Professional's declaration)
If "No", pls declare "No". If "Yes", pls elaborate on the changes.
M&V plan to determine energy consumption pre-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals
Photographic evidence of M&V instrumentation installed
Proposed M&V plan to determine energy consumption post-retrofit including the following details, where applicable: - parameters to be measured - details on instrumentation - duration - trending intervals - equations and/or simulation methodologies used to derive the consumption and performance
Calculations <For project team's proposal>

## Proposed Qualifying Costs
PROPOSED/ ESTIMATED QUALIFYING COSTS
Instructions
To complete all fields in this tab for all EIWs that the applicant is claiming under the scheme at Scheme Application stage 1. All fields under columns B to D must be completed. Column E is for BCA's internal processing. 2. To separately provide the relevant sections of the contracts as part of the complete application 3. Any goodwill discounts are to be reflected and will be less off from the qualifying costs 4. The total contract cost must tally with the total costs stated in the corresponding section in the contract document 5. Contract details for Chiller Plant and AHU have been collapsed as Air-Conditioning System 6. Pls add on contract details for other EIWs that applicant is claiming under the scheme under "Others", following the same format as the given template above.
| Contract Item S/N | Description of Energy Improvement Works | Proposed Qualifying Cost (by Applicant) | Estimated Qualifying Cost (to be completed by BCA)
Air-Conditioning System
| 2 | [Description of Contract Item] e.g. Replacement of Existing Chiller plant and pumps and airside system (Letter of Award ref. no: xxx dated 24 May 2022; awarded to xxx)
| 2.1 | Decommissioning & dismantling of 3 nos existing chiller, associated pipe & accessories. | 3000
| 2.2 | Decommissioning & dismantling of 5 nos existing air handling units, associated pipe & accessories. | 1000
| 2.3 | Decommissioning & dismantling of 16 nos existing fan coil units, associated pipe & accessories. | 500
| 2.4 | … | …
| 2.5 | … | …
| 2.6 | … | …
| 2.7 | … | …
|  | Sub-total | 4500 | 0
Mechanical Ventilation
| 3 | [Description of Contract Item] e.g. Replacement of Carpark MV Fan (Letter of Award ref. no: xxx dated 24 May 2022; awarded to xxx)
| 3.1 | … | …
| … | … | …
| … | … | …
| … | … | …
| … | … | …
| … | … | …
| … | … | …
|  | Sub-total | 0 | 0
Lighting
| 2 | [Description of Contract Item] e.g. Replacement of Existing Lightings to LED Lightings (Letter of Award ref. no: xxx dated 24 May 2022; awarded to xxx)
| 2.1 | Supply, installation, testing & commissioning of LED energy-efficient lighting to replace existing lighting, complete with fittings & necessary electrical work as per Lighting Schedule. | 10761
| … | … | …
| … | … | …
|  | Sub-total | 10761 | 0
Others (if applicable):
|  | Sub-total | 0 | 0
| TOTAL |  | 15261 | 0

## Proposal Summary
PROPOSAL SUMMARY
Instructions
At Scheme Application stage, 1. Ensure the details ported over from the individual 'System Level' tabs to the following tables are correct and to add on details for any additional proposed EIWs where applicable, to summarise the Total Estimated Energy Savings / Total Actual Energy Savings 2. Ensure the targeted Green Mark rating ported over from the 'Project Details' tab and the other auto-populated details are in order. 3. Ensure the detail ported over from the 'Proposed Qualifying Cost' tab to the 'Proposed Grant Amount' table is correct. 4. The Maximum Grant Amount is determined from the information in items 1, 2 and 3. At First Tranche Application stage, 5. Ensure the detail ported over from the 'Disbursement Application' tab to the 'First Tranche' table is correct. 6. The First tranche amount is determined from the Maximum Grant Amount and the information in item 5. At Second Tranche Application stage, 7. Ensure the Total Actual Energy Savings details ported over from the individual 'System Level' tabs to the following tables are correct and to add on details for any additional proposed EIWs where applicable. 8. Ensure the detail ported over from the 'Disbursement Application' tab to the 'Second Tranche' table is correct. 9. The Second tranche amount is determined from the information in items 7 and 8.
| Pre-Retrofit |  |  |  |  | Post-Retrofit
| Total Estimated Energy Savings |  |  |  |  | Total Actual Energy Savings
| Item | Energy Improvement Works (EIWs) | Estimated Energy Savings (kWh/yr) | Estimated Energy Savings obtained over Useful Lifespan (kWh) |  | Item | Energy Improvement Works (EIWs) | Actual Energy Savings (kWh/yr) | Actual Energy Savings obtained over Useful Lifespan (kWh)
|  |  |  | To assume equipment useful lifespan of 15 years |  |  |  |  | To assume equipment useful lifespan of 15 years
| 1 | Replacement of Chiller Plant | 1845076.5575 | 27676148.3619 |  | 1 | Replacement of Chiller Plant | 1903363.895 | 28550458.4243
| 2 | Replacement of AHUs/FCUs | 346678.8 | 5200182 |  | 2 | Replacement of AHUs/FCUs | 348702.9 | 5230543.5
| 3 | Replacement of Lighting | 0 | 0 |  | 3 | Replacement of Lighting | 0 | 0
| 4 | Mechanical Ventilation in Carpark | 16516.5 | 247747.5 |  | 4 | Mechanical Ventilation in Carpark | 0 | 0
| 5 | <To insert other measures, if any> |  | 0 |  | 5 | <To insert other measures, if any> |  | 0
| 6 | <To insert other measures, if any> |  | 0 |  | 6 | <To insert other measures, if any> |  | 0
| Total: |  |  | 33124077.8619 |  | Total: |  |  | 33781001.9243
|  | Proposed Grant Amount |  | Estimated Grant Amount |  |  | First Tranche
|  | Target Green Mark Rating | Platinum |  |  |  | Total First Tranche claim made by Applicant | 105332.5
|  | Funding Factor ($/tCO2e) | FALSE |  |  |  | Incentive cap based on 30% of Maximum Grant Amount | 0
|  | Estimated Energy Savings (kWh/yr) over useful lifespan | 33124077.8619 |  |  |  | First Tranche | 0
|  | Estimated Carbon Abated (tCO2e) | 13514.6238
|  | Estimated Grant Amount from Estimated Carbon Abated | 0
|  | Incentive cap based on target Green Mark rating | $600,000
|  | Incentive cap based on 50% of Proposed Qualifying Costs | 7630.5 | Incentive cap based on 50% of Estimated Qualifying Costs | 0 |  | Second Tranche
|  | Proposed Maximum Grant Amount | 0 | Maximum Grant Amount | 0 |  | Attained Green Mark Rating | Platinum
[7 empty] | Funding Factor ($/tCO2e) | 25
[7 empty] | Actual Energy Savings (kWh/yr) over useful lifespan | 33781001.9243
[7 empty] | Actual Carbon Abated (tCO2e) | 13782.6488
[7 empty] | Total Grant Amount from Actual Carbon Abated | 344566.2196
[7 empty] | Incentive cap based on Attained Green Mark Rating | $600,000
[7 empty] | Incentive cap based on 50% of total claims made by Applicant | 368663.75
[7 empty] | Maximum Grant Amount | 0
[7 empty] | Actual Grant Amount | 0
[7 empty] | Second Tranche (less First Tranche) | 0
Note on D15: <For project team to insert, if any>
Note on J15: <For project team to insert, if any>
Note on D16: <For project team to insert, if any>
Note on J16: <For project team to insert, if any>

## Disbursement Application
ACTUAL QUALIFYING COSTS
Instructions
At First and Second Tranche Application stage, columns A to H to be completed 1. Port over the relevant details on applicable items under 'Estimated Qualifying Costs' from the 'Proposed Qualifying Costs' tab to columns A to C in the table below and to add on details for any additional proposed EIWs where applicable. 2. Certified true copy of the payment receipts and the corresponding invoices of all EIWs are to be submitted as part of the complete application
Contract S/N | Description of Contract Item | Qualifying Cost | Description of Invoice | Invoice Ref No. | Payment Receipt Ref No. | Payment Receipt Date | Payment Receipt Amount | Disbursement Stage
2 | Replacement of Existing Chiller plant and pumps and airside system (Letter of Award ref. no: xxx dated 24 May 2022; awarded to xxx) | … | Downpayment at 10% |  | LOA001-2022-001 | 2022-10-10 | 105332.5 | First Tranche
2.1 |  |  | Milestone Payment 1 |  | LOA001-2022-002 | 2022-11-11 | 52666.25 | Second Tranche
2.2 |  |  | Milestone Payment 2 |  | … | … | 52666.25
2.3 |  |  | Milestone Payment 3 |  | … | … | 52666.25 | Second Tranche
2.4 |  |  | Milestone Payment 4 |  | … | … | 52666.25
2.5 |  |  | Milestone Payment 5 |  | … | … | 105332.5
2.6 |  |  | Milestone Payment 6 |  | … | … | 105332.5 | Second Tranche
2.7 |  |  | Milestone Payment 7 |  | … | … | 105332.5
… | … | … | … |  | … | … | 105332.5
… | … | … | … |  | … | … | …
… | … | … | … |  | … | … | …
… | … | … | … |  | … | … | …
… | … | … | … |  | … | … | …
… | … | … | … |  | … | … | …
Total Actual Qualifying Cost |  | 0
| Total Claims Till Date | 737327.5
| Total Payout as at First Tranche | 105332.5
| Total Payout as at Second Tranche | 210665

## Data Validation Sheet (hidden)
Platinum
Super Low Energy
Zero Energy